## Revision History
ControllerSunSpecMap.xls
This file contains the list of SunSpec registers and bitfields supported by the Mate3 and AXSPort communications controllers
This file is shipped with the ModBus Development Package.
Modified by:
Revision History |  |  | DE | Darren Emmons
|  |  | DKL | David LeBow
|  |  | BJM | Bryce Millet
|  |  | JSB | Jeff Bosch
|  |  | KN | Kanishk Nadkarni
Date | By | Comments
2017-04-17 | DE | Original document
2017-08-28 | BJM | Added new revision history page
2017-10-18 | DE | Added GSconfig_EE_Write_Enable to GSconfig block. Only used by ModBus
2018-12-11 | JSB | Changed OutBack_Alarm_Email_Subject_Line to OutBack_System_Name and changed size to 30. Changed size of OutBack_Alarm_Email_To_Address_1 to 15. Changed OutBack_Alarm_Email_Enable to OutBack_Gateway_Status_Buffer Added bitfield for OutBack_Gateway_Status_Buffer
2018-12-13 | VR | Added bitfield for ob_control_status (Absorb,bulk,sd card present,replay file present ,sd card error)
2018-12-17 | VR | Replaced Outback_Gateway_status_buffer with OutBack_Alarm_Email_Enable
2019-01-14 | JSB | GSconfig_AC_Coupled (SunSpecMap tab, DID 64116, row 433: a) R/W change to R b) Remove "(Not implemented)"
2019-07-29 | KN | Added GS_Split_GT_Number to DID 64115 and GS_Single_GT_Number to to DID 64117. Changed I_AC_PF units from % to N/A.

## SunSpecMap
Table 1 OutBack Block
DID | Start | End | Size | R/W | Field Name | Type | Units | Scale Factor | Contents | Description
64110 | 1 | 1 | 1 | R | OutBack_DID | uint16 | N/A | N/A | 64110 | Uniquely identifies this as a SunSpec Outback Interface
64110 | 2 | 2 | 1 | R | OutBack_Length | uint16 | Registers | N/A | 420 | Length of block in 16-bit registers
64110 | 3 | 3 | 1 | R | OutBack_Major_Firmware_Number | uint16 | N/A | N/A | Read Only | OutBack Major firmware revision
64110 | 4 | 4 | 1 | R | OutBack_Mid_Firmware_Number | uint16 | N/A | N/A | Read Only | OutBack Mid firmware revision
64110 | 5 | 6 | 1 | R | OutBack_Minor_Firmware_Number | uint16 | N/A | N/A | Read Only | OutBack Minor firmware revision
64110 | 6 | 6 | 1 | R | OutBack_Encryption_Key | uint16 | N/A | N/A | Read Only | Encryption key for current session (0 = Encryption not enabled)
64110 | 7 | 13 | 7 | R | OutBack_MAC_Address | string (14) | N/A | N/A | Read Only | Ethernet MAC address
64110 | 14 | 21 | 8 | W | OutBack_Write_Password | string (16) | N/A | N/A | Write Only | Password required to write to any register
64110 | 22 | 22 | 1 | R/W | OutBack_Enable_DHCP | uint16 | Enumerated | N/A | Programmable | 0 = DHCP Disabled, use configured network parameter; 1 = DHCP Enabled
64110 | 23 | 24 | 2 | R/W | OutBack_TCP/IP_Address | uint32 | Address | N/A | Programmable | TCP/IP Address xxx.xxx.xxx.xxx
64110 | 25 | 26 | 2 | R/W | OutBack_TCP/IP_Gateway_MSW | uint32 | Address | N/A | Programmable | TCP/IP Gateway xxx.xxx.xxx.xxx
64110 | 27 | 28 | 2 | R/W | OutBack_TCP/IP_Netmask_MSW | uint32 | Address | N/A | Programmable | TCP/IP Netmask xxx.xxx.xxx.xxx
64110 | 29 | 30 | 2 | R/W | OutBack_TCP/IP_DNS_1_MSW | uint32 | Address | N/A | Programmable | TCP/IP DNS 1 xxx.xxx.xxx.xxx
64110 | 31 | 32 | 2 | R/W | OutBack_TCP/IP_DNS_2_MSW | uint32 | Address | N/A | Programmable | TCP/IP DNS 2 xxx.xxx.xxx.xxx
64110 | 33 | 33 | 1 | R/W | OutBack_Modbus_Port | uint16 | N/A | N/A | Programmable | Outback MODBUS IP port, default 502
64110 | 34 | 53 | 20 | R/W | OutBack_SMTP_Server_Name | string (40) | N/A | N/A | Programmable | Email server name
64110 | 54 | 69 | 16 | R/W | OutBack_SMTP_Account_Name | string (32) | N/A | N/A | Programmable | Email account name
64110 | 70 | 70 | 1 | R/W | OutBack_SMTP_SSL_Enable | uint16 | Enumerated | N/A | Programmable | 0 = SSL Disabled; 1 = SSL Enabled (not implemented)
64110 | 71 | 78 | 8 | W | OutBack_SMTP_Email_Password | string 16) | N/A | N/A | Write Only | Email account password
64110 | 79 | 98 | 20 | R/W | OutBack_SMTP_Email_User_Name | string (40) | N/A | N/A | Programmable | Email account User Name
64110 | 99 | 99 | 1 | R/W | OutBack_Status_Email_Interval | uint16 | N/A | N/A | Programmable | 0 = Status Email Disabled, 1-23 Status Email every n hours
64110 | 100 | 100 | 1 | R/W | OutBack_Status_Email_Status_Time | uint16 | N/A | N/A | Programmable | Hour of first status email of the day
64110 | 101 | 125 | 25 | R/W | OutBack_Status_Email_Subject_Line | string (50) | N/A | N/A | Programmable | Status Email Subject Line
64110 | 126 | 145 | 20 | R/W | OutBack_Status_Email_To_Address_1 | string (40) | N/A | N/A | Programmable | Status Email to Address 1
64110 | 146 | 165 | 20 | R/W | OutBack_Status_Email_To_Address_2 | string (40) | N/A | N/A | Programmable | Status Email to Address 2
64110 | 166 | 166 | 1 | R/W | OutBack_Alarm_Email_Enable | uint16 | Enumerated | N/A | Programmable | 0 = Disabled; 1 = Enabled
64110 | 167 | 191 | 30 | R/W | OutBack_System_Name | string (60) | N/A | N/A | Programmable | OutBack System Name
64110 | 197 | 211 | 15 | R/W | OutBack_Alarm_Email_To_Address_1 | string (30) | N/A | N/A | Programmable | Status Alarm to Address 1
64110 | 212 | 231 | 20 | R/W | OutBack_Alarm_Email_To_Address_2 | string (40) | N/A | N/A | Programmable | Status Alarm to Address 2
64110 | 232 | 239 | 8 | W | OutBack_FTP_Password | string (16) | N/A | N/A | Write Only | FTP password
64110 | 240 | 247 | 8 | W | OutBack_Telnet_Password | string (16) | N/A | N/A | Write Only | Telnet password (not implemented)
64110 | 248 | 248 | 1 | R/W | OutBack_SD_Card_Data_Log_Write_Interval | uint16 | N/A | N/A | Programmable | 0 = SD-Card Data Logging disabled, 1-60 seconds
64110 | 249 | 249 | 1 | R/W | OutBack_SD_Card_Data_Log_Retain_Days | uint16 | N/A | N/A | Programmable | 0 = Log until SD-Card is full then erase oldest, 1-731 Number of days to retain data logs
64110 | 250 | 250 | 1 | R/W | OutBack_SD_Card_Data_Logging_Mode | uint16 | Enumerated | N/A | Programmable | 0 = Disabled; 1 = Excel Format; 2 = Compact Format
64110 | 251 | 270 | 20 | R/W | OutBack_Time_Server_Name | string (40) | N/A | N/A | Programmable | Timeserver domain name
64110 | 271 | 271 | 1 | R/W | OutBack_Enable_Time_Server | uint16 | Enumerated | N/A | Programmable | 0 = Time Server Disabled, use configured time parameters; 1 = Time Server Enabled
64110 | 272 | 272 | 1 | R/W | OutBack_Set_Time_Zone | int16 | Hours | OutBack_Time_Zone_SF | Programmable | Time Zone -12.0 … +14.0
64110 | 273 | 273 | 1 | R/W | OutBack_Enable_Float_Coordination | uint16 | N/A | N/A | Programmable | 0=Disabled, 1=Enabled
64110 | 274 | 274 | 1 | R/W | OutBack_Enable_FNDC_Charge_Termination | uint16 | N/A | N/A | Programmable | 0=Disabled, 1=Enabled
64110 | 275 | 275 | 1 | R/W | OutBack_Enable_FNDC_Grid_Tie_Control | uint16 | N/A | N/A | Programmable | 0=Disabled, 1=Enabled
64110 | 276 | 276 | 1 | R | OutBack_Voltage_SF | int16 | N/A | N/A | -1 | DC Voltage Scale Factor
64110 | 277 | 277 | 1 | R | OutBack_Hour_SF | int16 | N/A | N/A | -1 | Hours Scale Factor
64110 | 278 | 278 | 1 | R/W | OutBack_AGS_Mode | uint16 | Enumerated | N/A | Programmable | 0=Disabled, 1=Enabled
64110 | 279 | 279 | 1 | R/W | OutBack_AGS_Port | uint16 | N/A | N/A | Programmable | AGS device port number 0-10
64110 | 280 | 280 | 1 | R/W | OutBack_AGS_Port_Type | uint16 | Enumerated | N/A | Programmable | 0=Radian AUX Relay, 1=Radian AUX Output
64110 | 281 | 281 | 1 | R/W | OutBack_AGS_Generator_Type | uint16 | Enumerated | N/A | Programmable | 0=AC Gen, 1=DC Gen, 2=No Gen
64110 | 282 | 282 | 1 | R/W | OutBack_AGS_DC_Gen_Absorb_Voltage | uint16 | Volts | OutBack_Voltage_SF | Programmable | DC Generator Absorb Voltage
64110 | 283 | 283 | 1 | R/W | OutBack_AGS_DC_Gen_Absorb_Time | uint16 | Hour | OutBack_Hour_SF | Programmable | DC Generator Absorb Time
64110 | 284 | 284 | 1 | R/W | OutBack_AGS_Fault_Time | uint16 | Minutes | N/A | Programmable | AGS Generator fault time delay
64110 | 285 | 285 | 1 | R/W | OutBack_AGS_Gen_Cool_Down_Time | uint16 | Minutes | N/A | Programmable | AGS Generator Cool Down Time
64110 | 286 | 286 | 1 | R/W | OutBack_AGS_Gen_Warm_Up_Time | uint16 | Minutes | N/A | Programmable | AGS Generator Warm Up Time
64110 | 287 | 287 | 1 | R/W | OutBack_AGS_Generator_Exercise_Mode | uint16 | Enumerated | N/A | Programmable | 0=Disabled, 1=Enabled
64110 | 288 | 288 | 1 | R/W | OutBack_AGS_Exercise_Start_Hour | uint16 | Hour | N/A | Programmable | Exercise Start Hour 0-23
64110 | 289 | 289 | 1 | R/W | OutBack_AGS_Exercise_Start_Minute | uint16 | Minutes | N/A | Programmable | Exercise Start Minute 0-59
64110 | 290 | 290 | 1 | R/W | OutBack_AGS_Exercise_Day | uint16 | Enumerated | N/A | Programmable | 0=Sun, 1=Mon, 2=Tue, 3=Wed, 4=Thr, 5=Fri, 6=Sat
64110 | 291 | 291 | 1 | R/W | OutBack_AGS_Exercise_Period | uint16 | Minutes | N/A | Programmable | Exercise Period 1-240 minutes
64110 | 292 | 292 | 1 | R/W | OutBack_AGS_Exercise_Interval | uint16 | Weeks | N/A | Programmable | Exercise interval 1-8 Weeks
64110 | 293 | 293 | 1 | R/W | OutBack_AGS_Sell_Mode | uint16 | Enumerated | N/A | Programmable | Sell During Generator Exercise Period, 0=Selling Enabled, 1=Selling Disabled
64110 | 294 | 294 | 1 | R/W | OutBack_AGS_2_Min_Start_Mode | uint16 | Enumerated | N/A | Programmable | 0=Disabled, 1=Enabled
64110 | 295 | 295 | 1 | R/W | OutBack_AGS_2_Min_Start_Voltage | uint16 | Volts | OutBack_Voltage_SF | Programmable | Two Minute AGS Start Voltage
64110 | 296 | 296 | 1 | R/W | OutBack_AGS_2_Hour_Start_Mode | uint16 | Enumerated | N/A | Programmable | 0=Disabled, 1=Enabled
64110 | 297 | 297 | 1 | R/W | OutBack_AGS_2_Hour_Start_Voltage | uint16 | Volts | OutBack_Voltage_SF | Programmable | Two Hour AGS Start Voltage
64110 | 298 | 298 | 1 | R/W | OutBack_AGS_24_Hour_Start_Mode | uint16 | Enumerated | N/A | Programmable | 0=Disabled, 1=Enabled
64110 | 299 | 299 | 1 | R/W | OutBack_AGS_24_Hour_Start_Voltage | uint16 | Volts | OutBack_Voltage_SF | Programmable | Twenty Four Hour AGS Start Voltage
64110 | 300 | 300 | 1 | R/W | OutBack_AGS_Load_Start_Mode | uint16 | Enumerated | N/A | Programmable | 0=Disabled, 1=Enabled
64110 | 301 | 301 | 1 | R/W | OutBack_AGS_Load_Start_kW | uint16 | kWatts | N/A | Programmable | Load Start kWatts
64110 | 302 | 302 | 1 | R/W | OutBack_AGS_Load_Start_Delay | uint16 | Minutes | N/A | Programmable | Load Start Delay
64110 | 303 | 303 | 1 | R/W | OutBack_AGS_Load_Stop_kW | uint16 | kWatts | N/A | Programmable | Load Stop kWatts
64110 | 304 | 304 | 1 | R/W | OutBack_AGS_Load_Stop_Delay | uint16 | Minutes | N/A | Programmable | Load Stop Delay
64110 | 305 | 305 | 1 | R/W | OutBack_AGS_SOC_Start_Mode | uint16 | Enumerated | N/A | Programmable | 0=Disabled, 1=Enabled
64110 | 306 | 306 | 1 | R/W | OutBack_AGS_SOC_Start_Percentage | uint16 | Percent | N/A | Programmable | AGS SOC Start Percentage
64110 | 307 | 307 | 1 | R/W | OutBack_AGS_SOC_Stop_Percentage | uint16 | Percent | N/A | Programmable | AGS SOC Stop Percentage
64110 | 308 | 308 | 1 | R/W | OutBack_AGS_Enable_Full_Charge_Mode | uint16 | Enumerated | N/A | Programmable | 0=Disabled, 1=Enabled
64110 | 309 | 309 | 1 | R/W | OutBack_AGS_Full_Charge_Interval | uint16 | Days | N/A | Programmable | AGS SOC Full Charge Interval
64110 | 310 | 310 | 1 | R/W | OutBack_AGS_Must_Run_Mode | uint16 | Enumerated | N/A | Programmable | 0=Disabled, 1=Enabled
64110 | 311 | 311 | 1 | R/W | OutBack_AGS_Must_Run_Weekday_Start_Hour | uint16 | Hour | N/A | Programmable | AGS Must Run Weekday Start Hour 0-23
64110 | 312 | 312 | 1 | R/W | OutBack_AGS_Must_Run_Weekday_Start_Minute | uint16 | Minute | N/A | Programmable | AGS Must Run Weekday Start Minute 0-59
64110 | 313 | 313 | 1 | R/W | OutBack_AGS_Must_Run_Weekday_Stop_Hour | uint16 | Hour | N/A | Programmable | AGS Must Run Weekday Stop Hour 0-23
64110 | 314 | 314 | 1 | R/W | OutBack_AGS_Must_Run_Weekday_Stop_Minute | uint16 | Minute | N/A | Programmable | AGS Must Run Weekday Stop Minute 0-59
64110 | 315 | 315 | 1 | R/W | OutBack_AGS_Must_Run_Weekend_Start_Hour | uint16 | Hour | N/A | Programmable | AGS Must Run Weekend Start Hour 0-23
64110 | 316 | 316 | 1 | R/W | OutBack_AGS_Must_Run_Weekend_Start_Minute | uint16 | Minute | N/A | Programmable | AGS Must Run Weekend Start Minute 0-59
64110 | 317 | 317 | 1 | R/W | OutBack_AGS_Must_Run_Weekend_Stop_Hour | uint16 | Hour | N/A | Programmable | AGS Must Run Weekend Stop Hour 0-23
64110 | 318 | 318 | 1 | R/W | OutBack_AGS_Must_Run_Weekend_Stop_Minute | uint16 | Minute | N/A | Programmable | AGS Must Run Weekend Stop Minute 0-59
64110 | 319 | 319 | 1 | R/W | OutBack_AGS_Quiet_Time_Mode | uint16 | Enumerated | N/A | Programmable | 0=Disabled, 1=Enabled
64110 | 320 | 320 | 1 | R/W | OutBack_AGS_Quiet_Time_Weekday_Start_Hour | uint16 | Hour | N/A | Programmable | AGS Quiet Time Weekday Start Hour 0-23
64110 | 321 | 321 | 1 | R/W | OutBack_AGS_Quiet_Time_Weekday_Start_Minute | uint16 | Minute | N/A | Programmable | AGS Quiet Time Weekday Start Minute 0-59
64110 | 322 | 322 | 1 | R/W | OutBack_AGS_Quiet_Time_Weekday_Stop_Hour | uint16 | Hour | N/A | Programmable | AGS Quiet Time Weekday Stop Hour 0-23
64110 | 323 | 323 | 1 | R/W | OutBack_AGS_Quiet_Time_Weekday_Stop_Minute | uint16 | Minute | N/A | Programmable | AGS Quiet Time Weekday Stop Minute 0-59
64110 | 324 | 324 | 1 | R/W | OutBack_AGS_Quiet_Time_Weekend_Start_Hour | uint16 | Hour | N/A | Programmable | AGS Quiet Time Weekend Start Hour 0-23
64110 | 325 | 325 | 1 | R/W | OutBack_AGS_Quiet_Time_Weekend_Start_Minute | uint16 | Minute | N/A | Programmable | AGS Quiet Time Weekend Start Minute 0-59
64110 | 326 | 326 | 1 | R/W | OutBack_AGS_Quiet_Time_Weekend_Stop_Hour | uint16 | Hour | N/A | Programmable | AGS Quiet Time Weekend Stop Hour 0-23
64110 | 327 | 327 | 1 | R/W | OutBack_AGS_Quiet_Time_Weekend_Stop_Minute | uint16 | Minute | N/A | Programmable | AGS Quiet Time Weekend Stop Minute 0-59
64110 | 328 | 329 | 2 | R/W | OutBack_AGS_Total_Generator_Run_Time | uint32 | Hours | N/A | Programmable | AGS Generator Total Run Time in Seconds
64110 | 330 | 330 | 1 | R/W | OutBack_HBX_Mode | uint16 | Enumerated | N/A | Programmable | 0=Disabled, 1=Voltage Only, 2=SOC Only, 3=Both
64110 | 331 | 331 | 1 | R/W | OutBack_HBX_Grid_Connect_Voltage | uint16 | Volts | OutBack_Voltage_SF | Programmable | HBX Grid Connect Voltage
64110 | 332 | 332 | 1 | R/W | OutBack_HBX_Grid_Connect_Delay | uint16 | Hours | OutBack_Hour_SF | Programmable | HBX Grid Connect Delay
64110 | 333 | 333 | 1 | R/W | OutBack_HBX_Grid_Disconnect_Voltage | uint16 | Volts | OutBack_Voltage_SF | Programmable | HBX Grid Disconnect Voltage
64110 | 334 | 334 | 1 | R/W | OutBack_HBX_Grid_Disconnect_Delay | uint16 | Hours | OutBack_Hour_SF | Programmable | HBX Grid Disconnect Delay
64110 | 335 | 335 | 1 | R/W | OutBack_HBX_Grid_Connect_SOC | uint16 | Percent | N/A | Programmable | HBX Grid Connect SOC Percentage
64110 | 336 | 336 | 1 | R/W | OutBack_HBX_Grid_Disconnect_SOC | uint16 | Percent | N/A | Programmable | HBX Grid Disconnect SOC Percentage
64110 | 337 | 337 | 1 | R/W | OutBack_Grid_Use_Interval_1_Mode | uint16 | Enumerated | N/A | Programmable | 0=Disabled, 1=Enabled
64110 | 338 | 338 | 1 | R/W | OutBack_Grid_Use_Interval_1_Weekday_Start_Hour | uint16 | Hour | N/A | Programmable | Grid Use Interval 1 Weekday Start Hour 0-23
64110 | 339 | 339 | 1 | R/W | OutBack_Grid_Use_Interval_1_Weekday_Start_Minute | uint16 | Hour | N/A | Programmable | Grid Use Interval 1 Weekday Start Minute 0-59
64110 | 340 | 340 | 1 | R/W | OutBack_Grid_Use_Interval_1_Weekday_Stop_Hour | uint16 | Hour | N/A | Programmable | Grid Use Interval 1 Weekday Stop Hour 0-23
64110 | 341 | 341 | 1 | R/W | OutBack_Grid_Use_Interval_1_Weekday_Stop_Minute | uint16 | Hour | N/A | Programmable | Grid Use Interval 1 Weekday Stop Minute 0-59
64110 | 342 | 342 | 1 | R/W | OutBack_Grid_Use_Interval_1_Weekend_Start_Hour | uint16 | Hour | N/A | Programmable | Grid Use Interval 1 Weekend Start Hour 0-23
64110 | 343 | 343 | 1 | R/W | OutBack_Grid_Use_Interval_1_Weekend_Start_Minute | uint16 | Hour | N/A | Programmable | Grid Use Interval 1 Weekend Start Minute 0-59
64110 | 344 | 344 | 1 | R/W | OutBack_Grid_Use_Interval_1_Weekend_Stop_Hour | uint16 | Hour | N/A | Programmable | Grid Use Interval 1 Weekend Stop Hour 0-23
64110 | 345 | 345 | 1 | R/W | OutBack_Grid_Use_Interval_1_Weekend_Stop_Minute | uint16 | Hour | N/A | Programmable | Grid Use Interval 1 Weekend Stop Minute 0-59
64110 | 346 | 346 | 1 | R/W | OutBack_Grid_Use_Interval_2_Mode | uint16 | Enumerated | N/A | Programmable | 0=Disabled, 1=Enabled
64110 | 347 | 347 | 1 | R/W | OutBack_Grid_Use_Interval_2_Weekday_Start_Hour | uint16 | Hour | N/A | Programmable | Grid Use Interval 2 Weekday Start Hour 0-23
64110 | 348 | 348 | 1 | R/W | OutBack_Grid_Use_Interval_2_Weekday_Start_Minute | uint16 | Hour | N/A | Programmable | Grid Use Interval 2 Weekday Start Minute 0-59
64110 | 349 | 349 | 1 | R/W | OutBack_Grid_Use_Interval_2_Weekday_Stop_Hour | uint16 | Hour | N/A | Programmable | Grid Use Interval 2 Weekday Stop Hour 0-23
64110 | 350 | 350 | 1 | R/W | OutBack_Grid_Use_Interval_2_Weekday_Stop_Minute | uint16 | Hour | N/A | Programmable | Grid Use Interval 2 Weekday Stop Minute 0-59
64110 | 351 | 351 | 1 | R/W | OutBack_Grid_Use_Interval_3_Mode | uint16 | Enumerated | N/A | Programmable | 0=Disabled, 1=Enabled
64110 | 352 | 352 | 1 | R/W | OutBack_Grid_Use_Interval_3_Weekday_Start_Hour | uint16 | Hour | N/A | Programmable | Grid Use Interval 3 Weekday Start Hour 0-23
64110 | 353 | 353 | 1 | R/W | OutBack_Grid_Use_Interval_3_Weekday_Start_Minute | uint16 | Hour | N/A | Programmable | Grid Use Interval 3 Weekday Start Minute 0-59
64110 | 354 | 354 | 1 | R/W | OutBack_Grid_Use_Interval_3_Weekday_Stop_Hour | uint16 | Hour | N/A | Programmable | Grid Use Interval 3 Weekday Stop Hour 0-23
64110 | 355 | 355 | 1 | R/W | OutBack_Grid_Use_Interval_3_Weekday_Stop_Minute | uint16 | Hour | N/A | Programmable | Grid Use Interval 3 Weekday Stop Minute 0-59
64110 | 356 | 356 | 1 | R/W | OutBack_Load_Grid_Transfer_Mode | uint16 | Enumerated | N/A | Programmable | 0=Disabled, 1=Enabled
64110 | 357 | 357 | 1 | R/W | OutBack_Load_Grid_Transfer_Threshold | uint16 | kWatts | OutBack_Voltage_SF | Programmable | Load Grid Transfer Threshold kW
64110 | 358 | 358 | 1 | R/W | OutBack_Load_Grid_Transfer_Connect_Delay | uint16 | Seconds | N/A | Programmable | Load Grid Transfer Connect Delay Seconds
64110 | 359 | 359 | 1 | R/W | OutBack_Load_Grid_Transfer_Disconnect_Delay | uint16 | Seconds | N/A | Programmable | Load Grid Transfer Disconnect Delay Seconds
64110 | 360 | 360 | 1 | R/W | OutBack_Load_Grid_Transfer_Connect_Battery_Voltage | uint16 | Volts | OutBack_Voltage_SF | Programmable | Load Grid Transfer Low Battery Connect Voltage
64110 | 361 | 361 | 1 | R/W | OutBack_Load_Grid_Transfer_Re_Connect_Battery_Voltage | uint16 | Volts | OutBack_Voltage_SF | Programmable | Load Grid Transfer Low Battery Re-Connect Voltage
64110 | 362 | 362 | 1 | R/W | OutBack_Global_Charger_Control_Mode | uint16 | Enumerated | N/A | Programmable | 0=Disabled, 1=Enabled
64110 | 363 | 363 | 1 | R/W | OutBack_Global_Charger_Control_Output_Limit | uint16 | Amps | N/A | Programmable | Global Charger Output Limit Amps
64110 | 364 | 364 | 1 | R/W | OutBack_Radian_AC_Coupled_Control_Mode | uint16 | Enumerated | N/A | Programmable | 0=Disabled, 1=Enabled
64110 | 365 | 365 | 1 | R/W | OutBack_Radian_AC_Coupled_AUX_Port | uint16 | Port | N/A | Programmable | Radian Inverter Port Number for AUX Control 0-10
64110 | 366 | 367 | 2 | W | OutBack_URL_Update_Lock | uint32 | key | N/A | Write Only | Unlock Key
64110 | 368 | 387 | 20 | R/W | OutBack_Web_Reporting_Base_URL | string (40) | N/A | N/A | Programmable | WEB Reporting Base URL
64110 | 388 | 388 | 1 | R/W | OutBack_WEB_User_Logged_In_Status | uint16 | Enumerated | N/A | Programmable | 0=WEB User NOT logged in, 1=WEB user logged in
64110 | 389 | 389 | 1 | R | OutBack_HUB_Type | uint16 | Enumerated | N/A | Read Only | 0=Legecy HUB, 4= HUB4, 10=HUB10.3, 11=HUB3PH
64110 | 390 | 390 | 1 | R | OutBack_HUB_Major_Firmware_Number | uint16 | N/A | N/A | Read Only | HUB Major firmware revision
64110 | 391 | 391 | 1 | R | OutBack_HUB_Mid_Firmware_Number | uint16 | N/A | N/A | Read Only | HUB Mid firmware revision
64110 | 392 | 392 | 1 | R | OutBack_HUB_Minor_Firmware_Number | uint16 | N/A | N/A | Read Only | HUB Minor firmware revision
64110 | 393 | 393 | 1 | R/W | OutBack_Year | uint16 | N/A | N/A | Programmable | Clock year (4 digit)
64110 | 394 | 394 | 1 | R/W | Outback_Month | uint16 | N/A | N/A | Programmable | Clock Month (1 - 12)
64110 | 395 | 395 | 1 | R/W | OutBack_Day | uint16 | N/A | N/A | Programmable | Clock Day (1 - 31)
64110 | 396 | 396 | 1 | R/W | OutBack_Hour | uint16 | N/A | N/A | Programmable | Clock Hour (0 - 23)
64110 | 397 | 397 | 1 | R/W | Outback_Minute | uint16 | N/A | N/A | Programmable | Clock Minute (0 - 59)
64110 | 398 | 398 | 1 | R/W | OutBack_Second | uint16 | N/A | N/A | Programmable | Clock Second (0 - 59)
64110 | 399 | 399 | 1 | R | OutBack_Temp_Batt | int16 | Degrees C | N/A | Measured | Battery temp in degrees C
64110 | 400 | 400 | 1 | R | OutBack_Temp_Ambient | int16 | Degrees C | N/A | Measured | Ambient temp from temp sensor connected to device, in degrees C
64110 | 401 | 401 | 1 | R | OutBack_Temp_SF | int16 | N/A | N/A | 0 | Temperature Scale Factor
64110 | 402 | 402 | 1 | R | OutBack_Error | uint16 | Bitfield | N/A | Read Only | Bit field for errors. See Outback_Error Table
64110 | 403 | 403 | 1 | R | OutBack_Status | uint16 | Bitfield | N/A | Read Only | Bit field for status.See Outback_Status Table
64110 | 404 | 404 | 1 | R/W | OutBack_Update_Device_Firmware_Port | uint16 | Bitfield | N/A | Programmable | Device Firmware update See Device_FW_Update
64110 | 405 | 405 | 1 | R | OutBack_Gateway_Type | uint16 | Enumerated | N/A | Read Only | 1=AXS Port, 2= MATE3
64110 | 406 | 406 | 1 | R | OutBack_System_Voltage | uint16 | Volts | N/A | Read Only | 12, 24, 26, 48 or 60 VDC
64110 | 407 | 407 | 1 | R | OutBack_Measured_System_Voltage | uint16 | Volts | OutBack_Voltage_SF | Read Only | Current system battery voltage computed by gateway
64110 | 408 | 408 | 1 | R/W | OutBack_AGS_AC_Reconnect_Delay | uint16 | Minute | N/A | Programmable | AGS AC Reconnect Delay
64110 | 409 | 409 | 1 | R/W | OutBack_Multi_Phase_Coordination | uint16 | Enumerated | N/A | Programmable | 0=Disabled, 1=Enabled
64110 | 410 | 410 | 1 | R/W | OutBack_Sched_1_AC_Mode | int16 | Enumerated | N/A | Programmable | Scheduled Input Mode: -1=Disable, 0=Generator, 1=Support, 2=Grid Tied, 3=UPS, 4=Backup, 5=Mini Grid, 6=Grid Zero
64110 | 411 | 411 | 1 | R/W | OutBack_Sched_1_AC_Mode_Hour | uint16 | Hour | N/A | Programmable | Start Hour for AC Input Mode schedule 1
64110 | 412 | 412 | 1 | R/W | OutBack_Sched_1_AC_Mode_Minute | uint16 | Minute | N/A | Programmable | Start Minute for AC Input Mode schedule 1
64110 | 413 | 413 | 1 | R/W | OutBack_Sched_2_AC_Mode | int16 | Enumerated | N/A | Programmable | Scheduled Input Mode: -1=Disable, 0=Generator, 1=Support, 2=Grid Tied, 3=UPS, 4=Backup, 5=Mini Grid, 6=Grid Zero
64110 | 414 | 414 | 1 | R/W | OutBack_Sched_2_AC_Mode_Hour | uint16 | Hour | N/A | Programmable | Start Hour for AC Input Mode schedule 2
64110 | 415 | 415 | 1 | R/W | OutBack_Sched_2_AC_Mode_Minute | uint16 | Minute | N/A | Programmable | Start Minute for AC Input Mode schedule 2
64110 | 416 | 416 | 1 | R/W | OutBack_Sched_3_AC_Mode | int16 | Enumerated | N/A | Programmable | Scheduled Input Mode: -1=Disable, 0=Generator, 1=Support, 2=Grid Tied, 3=UPS, 4=Backup, 5=Mini Grid, 6=Grid Zero
64110 | 417 | 417 | 1 | R/W | OutBack_Sched_3_AC_Mode_Hour | uint16 | Hour | N/A | Programmable | Start Hour for AC Input Mode schedule 3
64110 | 418 | 418 | 1 | R/W | OutBack_Sched_3_AC_Mode_Minute | uint16 | Minute | N/A | Programmable | Start Minute for AC Input Mode schedule 3
64110 | 419 | 419 | 1 | R/W | OutBack_Auto_reboot | uint16 | Enumerated | N/A | Programmable | OPTICS auto reboot every 24 hours 0=Disable, 1=Enable
64110 | 420 | 420 | 1 | R | OutBack_Time_Zone_SF | int16 | N/A | N/A | -2 | Time Zone scale factor
64110 | 421 | 421 | 1 | R/W | OutBack_Spare_Reg_3 | uint16 | N/A | N/A | Programmable | Spare Register 3
64110 | 422 | 422 | 1 | R/W | OutBack_Spare_Reg_4 | uint16 | N/A | N/A | Programmable | Spare Register 4
420
Outback_Error Table
[9 empty] | Contents | Description
[9 empty] | 0x0001 | High limit last write
[9 empty] | 0x0002 | Low limit last write
[9 empty] | 0x0004 | Last write invalid
[9 empty] | 0x0008 | DHCP failed
[9 empty] | 0x0010 | DNS resolve failure
[9 empty] | 0x0020 | SMTP authorization failed
[9 empty] | 0x0040 | SMTP send failed
[9 empty] | 0x0080 | FTP Error
[9 empty] | 0x0100 | SD-Card Error
[9 empty] | 0x0200 | SNTP failure
[9 empty] | 0x0400 | Write while locked
[9 empty] | 0x0800 | Device firmware updating not supported
[9 empty] | 0x1000 | Device firmware update file not found
[9 empty] | 0x2000 | Device firmware update file invalid
[9 empty] | 0x4000 | Device firmware update failure
Outback_Status Table
[9 empty] | Contents | Description
[9 empty] | 0x0001 | Firmware update Complete
Device_FW_Update
[9 empty] | Contents | Description
[9 empty] | 0xPPXX | XX = device port number to update: 0-10
[9 empty] | 0xPPXX | PP = FW Update percent complete 0-100%
Table 2 Charge Controller Block
DID | Start | End | Size | R/W | Name | Type | Units | Scale Factor | Contents | Description
64111 | 1 | 1 | 1 | R | CC_DID | uint16 | N/A | N/A | 64111 | Uniquely identifies this as a SunSpec Basic Charge Controller
64111 | 2 | 2 | 1 | R | CC_Length | uint16 | Registers | N/A | 26 | Length of block in 16-bit registers
64111 | 3 | 3 | 1 | R | CC_Port_number | uint16 | N/A | N/A | 0-10 | Port number on Outback network
64111 | 4 | 4 | 1 | R | CC_Voltage_SF | int16 | N/A | N/A | -1 | DC Voltage Scale Factor
64111 | 5 | 5 | 1 | R | CC_Current_SF | int16 | N/A | N/A | -1 | DC Current Scale Factor
64111 | 6 | 6 | 1 | R | CC_Power_SF | int16 | N/A | N/A | 0 | DC Power Scale Factor
64111 | 7 | 7 | 1 | R | CC_AH_SF | int16 | N/A | N/A | 0 | DC Amp Hours Scale Factor
64111 | 8 | 8 | 1 | R | CC_KWH_SF | int16 | N/A | N/A | -1 | DC kWH Scale Factor
64111 | 9 | 9 | 1 | R | CC_Batt_Voltage | uint16 | Volts | CC_Voltage_SF | Measured | Battery Voltage
64111 | 10 | 10 | 1 | R | CC_Array_Voltage | uint16 | Volts | CC_Voltage_SF | Measured | DC Source Voltage
64111 | 11 | 11 | 1 | R | CC_Batt_Current | uint16 | Amps | CC_Current_SF | Measured | Battery Current
64111 | 12 | 12 | 1 | R | CC_Array_Current | uint16 | Amps | CC_Power_SF | Measured | DC Source Current
64111 | 13 | 13 | 1 | R | CC_Charger_State | uint16 | Enumerated | N/A | N/A | 0 = Silent; 1 = Float; 2 = Bulk; 3 = Absorb; 4 = EQ
64111 | 14 | 14 | 1 | R | CC_Watts | uint16 | Watts | CC_Power_SF | Measured | CC Wattage Output
64111 | 15 | 15 | 1 | R | CC_Todays_Min_Battery_Volts | uint16 | Volts | CC_Voltage_SF | Measured | Minimum Voltage for battery today
64111 | 16 | 16 | 1 | R | CC_Todays_Max_Battery_Volts | uint16 | Volts | CC_Voltage_SF | Measured | Maximum Voltage for battery today
64111 | 17 | 17 | 1 | R | CC_VOC | uint16 | Volts | CC_Voltage_SF | Measured | Last Open Circuit Voltage (array)
64111 | 18 | 18 | 1 | R | CC_Todays_Peak_VOC | uint16 | Volts | N/A | Measured | Highest VOC today
64111 | 19 | 19 | 1 | R | CC_Todays_kWH | uint16 | KWH | CC_KWH_SF | Measured | Daily accumulated Kwatt hours output
64111 | 20 | 20 | 1 | R | CC_Todays_AH | uint16 | AH | CC_AH_SF | Measured | Daily accumulated amp hours output
64111 | 21 | 21 | 1 | R | CC_Lifetime_kWH_Hours | uint16 | KWH | N/A | Measured | Lifetime Total Kwatt Hours
64111 | 22 | 22 | 1 | R | CC_Lifetime_kAmp_Hours | uint16 | Amps | CC_KWH_SF | Measured | Lifetime Total K-Amp Hours
64111 | 23 | 23 | 1 | R | CC_Lifetime_Max_Watts | uint16 | Watts | CC_Power_SF | Measured | Lifetime Maximum Wattage
64111 | 24 | 24 | 1 | R | CC_Lifetime_Max_Battery_Volts | uint16 | Volts | CC_Voltage_SF | Measured | Lifetime Maximum Battery Voltage
64111 | 25 | 25 | 1 | R | CC_Lifetime_Max_VOC | uint16 | Volts | CC_Voltage_SF | Measured | Lifetime Maximum VOC
64111 | 26 | 26 | 1 | R | CC_Temp_SF | uint16 | N/A | N/A | 0 | FM80 Extreme Temperature scale factor
64111 | 27 | 27 | 1 | R | CC_Temp_Output_FETs | int16 | Degrees C | CC_Power_SF | Measured | FM80 Extreme Output FET Temperature
64111 | 28 | 28 | 1 | R | CC_Temp_Enclosure | int16 | Degrees C | CC_Power_SF | Measured | FM80 Extreme Enclosure Temperature
Table 3 Charge Controller Configuration Block
DID | Start | End | Size | R/W | Name | Type | Units | Scale Factor | Contents | Description
64112 | 1 | 1 | 1 | R | CCconfig_DID | uint16 | N/A | N/A | 64112 | Vendor Extension for OutBack FM Series Charge Controllers
64112 | 2 | 2 | 1 | R | CCconfig_Length | uint16 | Registers | N/A | 88 | Length of block in 16-bit registers
64112 | 3 | 3 | 1 | R | CCconfig_Port_number | uint16 | N/A | N/A | 0-10 | Port number on Outback network
64112 | 4 | 4 | 1 | R | CCconfig_Voltage_SF | int16 | N/A | N/A | -1 | DC Voltage Scale Factor
64112 | 5 | 5 | 1 | R | CCconfig_Current_SF | int16 | N/A | N/A | -1 | DC Current Scale Factor
64112 | 6 | 6 | 1 | R | CCconfig_Hours_SF | int16 | N/A | N/A | -1 | Time in Hours Scale Factor
64112 | 7 | 7 | 1 | R | CCconfig_Power_SF | int16 | N/A | N/A | 0 | Power Scale Factor
64112 | 8 | 8 | 1 | R | CCconfig_AH_SF | int16 | N/A | N/A | 0 | Amp Hours Scale Factor
64112 | 9 | 9 | 1 | R | CCconfig_KWH_SF | int16 | N/A | N/A | -1 | DC kWH Scale Factor
64112 | 10 | 10 | 1 | R | CCconfig_Faults | uint16 | Bitfield | N/A | N/A | CC Error Flags: 0x0080=High VOC, 0x0040=Over Temp, 0x0020=Shorted Battery Temp Sensor, 0x0010=Fault Input Active
64112 | 11 | 11 | 1 | R/W | CCconfig_Absorb_Volts | uint16 | Volts | CCconfig_Voltage_SF | Programmable | Absorb Voltage Target
64112 | 12 | 12 | 1 | R/W | CCconfig_Absorb_Time_Hours | uint16 | Hours | CCconfig_Hours_SF | Programmable | Absorb Time Hours
64112 | 13 | 13 | 1 | R/W | CCconfig_Absorb_End_Amps | uint16 | Amps | N/A | Programmable | Amperage to end Absorbing
64112 | 14 | 14 | 1 | R/W | CCconfig_Rebulk_Volts | uint16 | Volts | CCconfig_Voltage_SF | Programmable | Voltage to re-initiate Bulk charge
64112 | 15 | 15 | 1 | R/W | CCconfig_Float_Volts | uint16 | Volts | CCconfig_Voltage_SF | Programmable | Float Voltage Target
64112 | 16 | 16 | 1 | R/W | CCconfig_Bulk_Current | uint16 | Amps | CCconfig_Current_SF | Programmable | Max Output Current Limit
64112 | 17 | 17 | 1 | R/W | CCconfig_EQ_Volts | uint16 | Volts | CCconfig_Voltage_SF | Programmable | Target Voltage for Equalize
64112 | 18 | 18 | 1 | R/W | CCconfig_EQ_Time_Hours | uint16 | Hours | N/A | Programmable | EQ Time Hours
64112 | 19 | 19 | 1 | R/W | CCconfig_Auto_EQ_Days | uint16 | Days | N/A | Programmable | Auto EQ Interval Days
64112 | 20 | 20 | 1 | R/W | CCconfig_MPPT_Mode | uint16 | Enumerated | N/A | Programmable | 0 = Auto; 1 = U-Pick
64112 | 21 | 21 | 1 | R/W | CCconfig_Sweep_Width | uint16 | Enumerated | N/A | Programmable | 0 = Full; 1 = Half
64112 | 22 | 22 | 1 | R/W | CCconfig_Sweep_Max_Percentage | uint16 | Enumerated | N/A | Programmable | 0 = 80; 1 = 85; 2 = 90; 3 = 99
64112 | 23 | 23 | 1 | R/W | CCconfig_U_Pick_PWM_Duty_Cycle | uint16 | Percentage | CCconfig_Voltage_SF | Programmable | Park Duty Cycle (%) (40% - 90%)
64112 | 24 | 24 | 1 | R/W | CCconfig_Grid_Tie_Mode | uint16 | Enumerated | N/A | Programmable | 0 = Grid Tie Mode disabled; 1 = Grid Tie Mode enabled
64112 | 25 | 25 | 1 | R/W | CCconfig_Temp_Comp_Mode | uint16 | Enumerated | N/A | Programmable | 0 = Wide; 1 = User Limited
64112 | 26 | 26 | 1 | R/W | CCconfig_Temp_Comp_Lower_Limit_Volts | uint16 | Volts | CCconfig_Voltage_SF | Programmable | RTS compensation lower voltage limit
64112 | 27 | 27 | 1 | R/W | CCconfig_Temp_Comp_Upper_Limit_Volts | uint16 | Volts | CCconfig_Voltage_SF | Programmable | RTS compensation upper voltage limit
64112 | 28 | 28 | 1 | R/W | CCconfig_Temp_Comp_Slope | uint16 | Milli Volts | N/A | Programmable | RTS temp compensation Slope 2-6 mV per Degree C
64112 | 29 | 29 | 1 | R/W | CCconfig_Auto_Restart_Mode | uint16 | Enumerated | N/A | Programmable | 0 = Off; 1 = Restart every 90 minutes; 2 = Restart every 90 minutes if absorb charging or float charging
64112 | 30 | 30 | 1 | R/W | CCconfig_Wakeup_VOC | uint16 | Volts | CCconfig_Voltage_SF | Programmable | VOC change which causes Wakeup occurs
64112 | 31 | 31 | 1 | R/W | CCconfig_Snooze_Mode_Amps | uint16 | Amps | CCconfig_Voltage_SF | Programmable | Snooze Mode Amps
64112 | 32 | 32 | 1 | R/W | CCconfig_Wakeup_Interval | uint16 | Mins | N/A | Programmable | How often to check for Wakeup condition
64112 | 33 | 33 | 1 | R/W | CCconfig_AUX_Mode | uint16 | Enumerated | N/A | Programmable | 0 = Float; 1 = Diversion: Relay; 2 = Diversion: Solid St; 3 = Low Batt Disconnect; 4 = Remote; 5 = Vent Fan; 6 = PV Trigger; 7 = Error Output; 8 = Night Light
64112 | 34 | 34 | 1 | R/W | CCconfig_AUX_Control | uint16 | Enumerated | N/A | Programmable | 0 = Off; 1 = Auto; 2 = On
64112 | 35 | 35 | 1 | R | CCconfig_AUX_State | uint16 | Enumerated | N/A | Read Only | 0 = Disabled; 1 = Enabled
64112 | 36 | 36 | 1 | R/W | CCconfig_AUX_Polarity | uint16 | Enumerated | N/A | Programmable | 0 = Low; 1 = High
64112 | 37 | 37 | 1 | R/W | CCconfig_AUX_Low_Batt_Disconnect | uint16 | Volts | CCconfig_Voltage_SF | Programmable | Low Battery Disconnect Voltage
64112 | 38 | 38 | 1 | R/W | CCconfig_AUX_Low_Batt_Reconnect | uint16 | Volts | CCconfig_Voltage_SF | Programmable | Low Battery Reconnect Volts
64112 | 39 | 39 | 1 | R/W | CCconfig_AUX_Low_Batt_Disconnect_Delay | uint16 | Secs | N/A | Programmable | Low Battery Disconnect Delay (secs)
64112 | 40 | 40 | 1 | R/W | CCconfig_AUX_Vent_Fan_Volts | uint16 | Volts | CCconfig_Voltage_SF | Programmable | Vent Fan Voltage
64112 | 41 | 41 | 1 | R/W | CCconfig_AUX_PV_Limit_Volts | uint16 | Volts | CCconfig_Voltage_SF | Programmable | Voltage at which PV disconnect occurs
64112 | 42 | 42 | 1 | R/W | CCconfig_AUX_PV_Limit_Hold_Time | uint16 | Secs | CCconfig_Hours_SF | Programmable | AUX PV Trigger Hold Time
64112 | 43 | 43 | 1 | R/W | CCconfig_AUX_Night_Light_Thres_Volts | uint16 | Volts | CCconfig_Voltage_SF | Programmable | Voltage Threshold for AUX Night Light
64112 | 44 | 44 | 1 | R/W | CCconfig_Night_Light_ON_Hours | uint16 | Hours | N/A | Programmable | Night Light ON Time
64112 | 45 | 45 | 1 | R/W | CCconfig_Night_Light_ON_Hyst_Time | uint16 | Mins | N/A | Programmable | Night Light ON Hyst Time
64112 | 46 | 46 | 1 | R/W | CCconfig_Night_Light_OFF_Hyst_Time | uint16 | Mins | N/A | Programmable | Night Light OFF Hyst Time
64112 | 47 | 47 | 1 | R/W | CCconfig_AUX_Error_Battery_Volts | uint16 | Volts | CCconfig_Voltage_SF | Programmable | Battery voltage at which Aux Error occurs
64112 | 48 | 48 | 1 | R/W | CCconfig_AUX_Divert_Hold_Time | uint16 | Seconds | CCconfig_Hours_SF | Programmable | AUX Diver Hold Time
64112 | 49 | 49 | 1 | R/W | CCconfig_AUX_Divert_Delay_Time | uint16 | Secs | N/A | Programmable | AUX Divert Delay
64112 | 50 | 50 | 1 | R/W | CCconfig_AUX_Divert_Relative_Volts | int16 | Volts | CCconfig_Voltage_SF | Programmable | AUX Divert Relative Volts
64112 | 51 | 51 | 1 | R/W | CCconfig_AUX_Divert_Hyst_Volts | uint16 | Volts | CCconfig_Voltage_SF | Programmable | AUX Divert Hyst Volts
64112 | 52 | 52 | 1 | R | CCconfig_Major_Firmware_Number | uint16 | N/A | N/A | Read Only | Charge Controller Major firmware revision
64112 | 53 | 53 | 1 | R | CCconfig_Mid_Firmware_Number | uint16 | N/A | N/A | Read Only | Charge Controller Mid firmware revision
64112 | 54 | 54 | 1 | R | CCconfig_Minor_Firmware_Number | uint16 | N/A | N/A | Read Only | Charge Controller Minor firmware revision
64112 | 55 | 55 | 1 | R/W | CCconfig_Set_Data_Log_Day_Offset | uint16 | Days | N/A | Programmable | Day offset 0-128, 0 =Today, 1 = -1 day …
64112 | 56 | 56 | 1 | R | CCconfig_Get_Current_Data_Log_Day_Offset | uint16 | Days | N/A | Read Only | Current Data Log Day Offset
64112 | 57 | 57 | 1 | R | CCconfig_Data_Log_Daily_AH | uint16 | AH | CCconfig_AH_SF | Read Only | Data Log AH
64112 | 58 | 58 | 1 | R | CCconfig_Data_Log_Daily_kWH | uint16 | KWH | CCconfig_KWH_SF | Read Only | Data Log kWH
64112 | 59 | 59 | 1 | R | CCconfig_Data_Log_Daily_Max_Output_Amps | uint16 | Amps | CCconfig_Voltage_SF | Read Only | Data Log maximum Output Amps
64112 | 60 | 60 | 1 | R | CCconfig_Data_Log_Daily_Max_Output_Watts | uint16 | Watts | CCconfig_Power_SF | Read Only | Data Log maximum Output Wattage
64112 | 61 | 61 | 1 | R | CCconfig_Data_Log_Daily_Absorb_Time | uint16 | Mins | N/A | Read Only | Data Log Absorb Time Minutes
64112 | 62 | 62 | 1 | R | CCconfig_Data_Log_Daily_Float_Time | uint16 | Mins | N/A | Read Only | Data Log Float Time Minutes
64112 | 63 | 63 | 1 | R | CCconfig_Data_Log_Daily_Min_Batt_Volts | uint16 | Volts | CCconfig_Voltage_SF | Read Only | Data Log minimum daily battery voltage
64112 | 64 | 64 | 1 | R | CCconfig_Data_Log_Daily_Max_Batt_Volts | uint16 | Volts | CCconfig_Voltage_SF | Read Only | Data Log maximum daily battery voltage
64112 | 65 | 65 | 1 | R | CCconfig_Data_Log_Daily_Max_Input_Volts | uint16 | Volts | N/A | Read Only | Data Log maximum daily input voltage
64112 | 66 | 66 | 1 | R | CCconfig_Clear_Data_Log_Read | uint16 | N/A | N/A | Read Only | Read value needed to clear data log
64112 | 67 | 67 | 1 | W | CCconfig_Clear_Data_Log_Write_Complement | uint16 | N/A | N/A | Write Only | Write value's complement to clear data log
64112 | 68 | 68 | 1 | R | CCconfig_Stats_Maximum_Reset_Read | uint16 | N/A | N/A | Read Only | Read value needed to clear Stats Maximums
64112 | 69 | 69 | 1 | W | CCconfig_Stats_Maximum_Write_Complement | uint16 | N/A | N/A | Write Only | Write value's complement to clear Stats Maximums
64112 | 70 | 70 | 1 | R | CCconfig_Stats_Totals_Reset_Read | uint16 | N/A | N/A | Read Only | Read value nneded to clear Stats Totals
64112 | 71 | 71 | 1 | W | CCconfig_Stats_Totals_Write_Complement | uint16 | N/A | N/A | Write Only | Write value's complement to clear Stats Totals
64112 | 72 | 72 | 1 | R/W | CCconfig_Battery_Voltage_Calibrate_Offset | int16 | DC Volts | CCconfig_Voltage_SF | Programmable | Battery voltage calibration offset
64112 | 73 | 81 | 9 | R | CCconfig_Serial_Number | string (18) | N/A | N/A | Read Only | Device serial number
64112 | 82 | 90 | 9 | R | CCconfig_Model_Number | string (18) | N/A | N/A | Read Only | Device model
Table 4 Split Phase Radian Inverter Real Time Block
DID | Start | End | Size | R/W | Name | Type | Units | Scale Factor | Contents | Description
64115 | 1 | 1 | 1 | R | GS_Split_DID | uint16 | N/A | N/A | 64115 | Vendor Extension for OutBack Radian Series Split Phase Inverter Status Block
64115 | 2 | 2 | 1 | R | GS_Split_Length | uint16 | Registers | N/A | 59 | Length of block in 16-bit registers
64115 | 3 | 3 | 1 | R | GS_Split_Port_number | uint16 | N/A | N/A | 0-10 | Port number on Outback network
64115 | 4 | 4 | 1 | R | GS_Split_DC_Voltage_SF | int16 | N/A | N/A | -1 | DC Voltage Scale Factor
64115 | 5 | 5 | 1 | R | GS_Split_AC_Current_SF | int16 | N/A | N/A | 0 | AC Current Scale Factor
64115 | 6 | 6 | 1 | R | GS_Split_AC_Voltage_SF | int16 | N/A | N/A | 0 | AC Voltage Scale Factor
64115 | 7 | 7 | 1 | R | GS_Split_AC_Frequency_SF | int16 | N/A | N/A | -1 | AC Frequency Scale Factor
64115 | 8 | 8 | 1 | R | GS_Split_L1_Inverter_Output_Current | int16 | Amps | GS_Split_AC_Current_SF | Measured | L1 inverter output current
64115 | 9 | 9 | 1 | R | GS_Split_L1_Inverter_Charge_Current | int16 | Amps | GS_Split_AC_Current_SF | Measured | L1 inverter charger current
64115 | 10 | 10 | 1 | R | GS_Split_L1_Inverter_Buy_Current | int16 | Amps | GS_Split_AC_Current_SF | Measured | L1 inverter buy current
64115 | 11 | 11 | 1 | R | GS_Split_L1_Inverter_Sell_Current | int16 | Amps | GS_Split_AC_Current_SF | Measured | L1 inverter sell current
64115 | 12 | 12 | 1 | R | GS_Split_L1_Grid_Input_AC_Voltage | int16 | Volts AC | GS_Split_AC_Voltage_SF | Measured | L1 Grid Input AC Voltage
64115 | 13 | 13 | 1 | R | GS_Split_L1_Gen_Input_AC_Voltage | int16 | Volts AC | GS_Split_AC_Voltage_SF | Measured | L1 Gen Input AC Voltage
64115 | 14 | 14 | 1 | R | GS_Split_L1_Output_AC_Voltage | int16 | Volts AC | GS_Split_AC_Voltage_SF | Measured | L1 Output AC Voltage
64115 | 15 | 15 | 1 | R | GS_Split_L2_Inverter_Output_Current | int16 | Amps | GS_Split_AC_Current_SF | Measured | L2 inverter output current
64115 | 16 | 16 | 1 | R | GS_Split_L2_Inverter_Charge_Current | int16 | Amps | GS_Split_AC_Current_SF | Measured | L2 inverter charger current
64115 | 17 | 17 | 1 | R | GS_Split_L2_Inverter_Buy_Current | int16 | Amps | GS_Split_AC_Current_SF | Measured | L2 inverter buy current
64115 | 18 | 18 | 1 | R | GS_Split_L2_Inverter_Sell_Current | int16 | Amps | GS_Split_AC_Current_SF | Measured | L2 inverter sell current
64115 | 19 | 19 | 1 | R | GS_Split_L2_Grid_Input_AC_Voltage | int16 | Volts AC | GS_Split_AC_Voltage_SF | Measured | L2 Grid Input AC Voltage
64115 | 20 | 20 | 1 | R | GS_Split_L2_Gen_Input_AC_Voltage | int16 | Volts AC | GS_Split_AC_Voltage_SF | Measured | L2 Gen Input AC Voltage
64115 | 21 | 21 | 1 | R | GS_Split_L2_Output_AC_Voltage | int16 | Volts AC | GS_Split_AC_Voltage_SF | Measured | L2 Output AC Voltage
64115 | 22 | 22 | 1 | R | GS_Split_Inverter_Operating_mode | int16 | Enumerated | N/A | Read Only | 0=Off, 1=Searching, 2=Inverting, 3=Charging, 4=Silent, 5=Float, 6=EQ, 7=Charger Off, 8=Support, 9=Selling, 10=Pass through, 14=Offsetting
64115 | 23 | 23 | 1 | R | GS_Split_Error_Flags | int16 | Bitfield | N/A | N/A | Bit field for errors. See GS_Error table
64115 | 24 | 24 | 1 | R | GS_Split_Warning_Flags | int16 | Bitfield | N/A | N/A | Bit field for warnings See GS_Warning table
64115 | 25 | 25 | 1 | R | GS_Split_Battery_Voltage | int16 | Volts DC | GS_Split_DC_Voltage_SF | Measured | Battery Voltage
64115 | 26 | 26 | 1 | R | GS_Split_Temp_Compensated_Target_Voltage | int16 | Volts DC | GS_Split_DC_Voltage_SF | Read Only | Temperature compensated target battery voltage
64115 | 27 | 27 | 1 | R | GS_Split_AUX_Output_State | int16 | Enumerated | N/A | N/A | 0 = Disabled; 1 = Enabled
64115 | 28 | 28 | 1 | R | GS_Split_AUX_Relay_Output_State | int16 | Enumerated | N/A | N/A | 0 = Disabled; 1 = Enabled
64115 | 29 | 29 | 1 | R | GS_Split_L_Module_Transformer_Temperature | int16 | Degrees C | N/A | Measured | Left module transformer temp in degrees C
64115 | 30 | 30 | 1 | R | GS_Split_L_Module_Capacitor_Temperature | int16 | Degrees C | N/A | Measured | Left module capacitor temp in degrees C
64115 | 31 | 31 | 1 | R | GS_Split_L_Module_FET_Temperature | int16 | Degrees C | N/A | Measured | Left module FET temp in degrees C
64115 | 32 | 32 | 1 | R | GS_Split_R_Module_Transformer_Temperature | int16 | Degrees C | N/A | Measured | Right module transformer temp in degrees C
64115 | 33 | 33 | 1 | R | GS_Split_R_Module_Capacitor_Temperature | int16 | Degrees C | N/A | Measured | Right module capacitor temp in degrees C
64115 | 34 | 34 | 1 | R | GS_Split_R_Module_FET_Temperature | int16 | Degrees C | N/A | Measured | Right module FET temp in degrees C
64115 | 35 | 35 | 1 | R | GS_Split_Battery_Temperature | int16 | Degrees C | N/A | Measured | Battery temp in degrees C
64115 | 36 | 36 | 1 | R | GS_Split_AC_Input_Selection | int16 | Enumerated | N/A | Read Only | 0=Grid, 1=Gen
64115 | 37 | 37 | 1 | R | GS_Split_AC_Input_Frequency | int16 | Hz | GS_Split_AC_Frequency_SF | Measured | Selected AC Input frequency HZ
64115 | 38 | 38 | 1 | R | GS_Split_AC_Input_Voltage | int16 | Volts AC | GS_Split_AC_Voltage_SF | Measured | Selected Input AC Voltage
64115 | 39 | 39 | 1 | R | GS_Split_AC_Input_State | int16 | Enumerated | N/A | N/A | 1=AC Use, 0=AC_Drop
64115 | 40 | 40 | 1 | R | GS_Split_Minimum_AC_Input_Voltage | int16 | Volts AC | GS_Split_AC_Voltage_SF | Read Only | Minimum Input AC Voltage (Write to clear stored value)
64115 | 41 | 41 | 1 | R | GS_Split_Maximum_AC_Input_Voltage | int16 | Volts AC | GS_Split_AC_Voltage_SF | Read Only | Maximum Input AC Voltage (Write to clear stored value)
64115 | 42 | 42 | 1 | R | GS_Split_Sell_Status | int16 | Bitfield | N/A | N/A | Bit field for sell status See GS_Sell_Status table
64115 | 43 | 43 | 1 | R | GS_Split_kWh_SF | int16 | N/A | N/A | -1 | AC kWh scale factor
64115 | 44 | 44 | 1 | R | GS_Split_AC1_L1_Buy_kWh | uint16 | kWh | GS_Split_kWh_SF | Measured | Daily AC1 Buy L1 kWh
64115 | 45 | 45 | 1 | R | GS_Split_AC2_L1_Buy_kWh | uint16 | kWh | GS_Split_kWh_SF | Measured | Daily AC2 Buy L1 kWh
64115 | 46 | 46 | 1 | R | GS_Split_AC1_L1_Sell_kWh | uint16 | kWh | GS_Split_kWh_SF | Measured | Daily AC1 Sell L1 kWh
64115 | 47 | 47 | 1 | R | GS_Split_AC2_L1_Sell_kWh | uint16 | kWh | GS_Split_kWh_SF | Measured | Daily AC2 Sell L1 kWh
64115 | 48 | 48 | 1 | R | GS_Split_L1_Output_kWh | uint16 | kWh | GS_Split_kWh_SF | Measured | Daily Output L1 kWh
64115 | 49 | 49 | 1 | R | GS_Split_AC1_L2_Buy_kWh | uint16 | kWh | GS_Split_kWh_SF | Measured | Daily AC1 Buy L2 kWh
64115 | 50 | 50 | 1 | R | GS_Split_AC2_L2_Buy_kWh | uint16 | kWh | GS_Split_kWh_SF | Measured | Daily AC1 Sell L2 kWh
64115 | 51 | 51 | 1 | R | GS_Split_AC1_L2_Sell_kWh | uint16 | kWh | GS_Split_kWh_SF | Measured | Daily AC1 Sell L2 kWh
64115 | 52 | 52 | 1 | R | GS_Split_AC2_L2_Sell_kWh | uint16 | kWh | GS_Split_kWh_SF | Measured | Daily AC2 Sell L2 kWh
64115 | 53 | 53 | 1 | R | GS_Split_L2_Output_kWh | uint16 | kWh | GS_Split_kWh_SF | Measured | Daily Output L2 kWh
64115 | 54 | 54 | 1 | R | GS_Split_Charger_kWh | uint16 | kWh | GS_Split_kWh_SF | Measured | Daily Charger kWh
64115 | 55 | 55 | 1 | R | GS_Split_Output_kW | uint16 | kW | GS_Split_kWh_SF | Measured | Output kW
64115 | 56 | 56 | 1 | R | GS_Split_Buy_kW | uint16 | kW | GS_Split_kWh_SF | Measured | Buy kW
64115 | 57 | 57 | 1 | R | GS_Split_Sell_kW | uint16 | kW | GS_Split_kWh_SF | Measured | Sell kW
64115 | 58 | 58 | 1 | R | GS_Split_Charge_kW | uint16 | kW | GS_Split_kWh_SF | Measured | Charge kW
64115 | 59 | 59 | 1 | R | GS_Split_Load_kW | uint16 | kW | GS_Split_kWh_SF | Measured | Load kW
64115 | 60 | 60 | 1 | R | GS_Split_AC_Couple_kW | uint16 | kW | GS_Split_kWh_SF | Measured | AC Coupled kW
64115 | 61 | 61 | 1 | R | GS_Split_GT_Number | uint16 | N/A | N/A | Measured | GT Number sent from Inverter to Charge Controller
59
GS_Error Table
[9 empty] | Contents | Description
[9 empty] | 0x0001 | Low AC output voltage
[9 empty] | 0x0002 | Stacking error
[9 empty] | 0x0004 | Over temperature error
[9 empty] | 0x0008 | Low battery voltage
[9 empty] | 0x0010 | Phase loss
[9 empty] | 0x0020 | High battery voltage
[9 empty] | 0x0040 | AC output shorted
[9 empty] | 0x0080 | AC backfeed
GS_Warning Table
[9 empty] | Contents | Description
[9 empty] | 0x0001 | AC input frequency too high
[9 empty] | 0x0002 | AC input frequency too low
[9 empty] | 0x0004 | AC input voltage too low
[9 empty] | 0x0008 | AC input voltage too high
[9 empty] | 0x0010 | AC input current exceeds max
[9 empty] | 0x0020 | Temperature sensor bad
[9 empty] | 0x0040 | Communications error
[9 empty] | 0x0080 | Cooling fan fault
GS_Sell_Status Table
[9 empty] | Contents | Description
[9 empty] | 0x0001 | AC input frequency too high
[9 empty] | 0x0002 | AC input frequency too low
[9 empty] | 0x0004 | AC input voltage too low
[9 empty] | 0x0008 | AC input voltage too high
[9 empty] | 0x0010 | Awaiting sell delay
[9 empty] | 0x0020 | Sell disabled
[9 empty] | 0x0040 | Battery voltage less than target
Table 5 Radian Inverter Configuration Block
DID | Start | End | Size | R/W | Name | Type | Units | Scale Factor | Contents | Description
64116 | 1 | 1 | 1 | R | GSconfig_DID | uint16 | N/A | N/A | 64116 | Vendor Extension for OutBack Radian Series Split Phase Inverter Configuration Block
64116 | 2 | 2 | 1 | R | GSconfig_Length | uint16 | Registers | N/A | 89 | Length of block in 16-bit registers
64116 | 3 | 3 | 1 | R | GSconfig_Port_number | uint16 | N/A | N/A | 0-10 | Port number on Outback network
64116 | 4 | 4 | 1 | R | GSconfig_DC_Voltage_SF | int16 | N/A | N/A | -1 | DC Voltage Scale Factor
64116 | 5 | 5 | 1 | R | GSconfig_AC_Current_SF | int16 | N/A | N/A | -1 | AC Current Scale Factor
64116 | 6 | 6 | 1 | R | GSconfig_AC_Voltage_SF | int16 | N/A | N/A | 0 | AC Voltage Scale Factor
64116 | 7 | 7 | 1 | R | GSconfig_Time_SF | int16 | N/A | N/A | -1 | Time Scale Factor
64116 | 8 | 8 | 1 | R | GSconfig_Major_Firmware_Number | uint16 | N/A | N/A | Read Only | Inverter Major firmware revision
64116 | 9 | 9 | 1 | R | GSconfig_Mid_Firmware_Number | uint16 | N/A | N/A | Read Only | Inverter Mid firmware revision
64116 | 10 | 10 | 1 | R | GSconfig_Minor_Firmware_Number | uint16 | N/A | N/A | Read Only | Inverter Minor firmware revision
64116 | 11 | 11 | 1 | R/W | GSconfig_Absorb_Volts | uint16 | DC Volts | GSconfig_DC_Voltage_SF | Programmable | Absorb Voltage Target
64116 | 12 | 12 | 1 | R/W | GSconfig_Absorb_Time_Hours | uint16 | Hours | GSconfig_Time_SF | Programmable | Absorb Time Hours
64116 | 13 | 13 | 1 | R/W | GSconfig_Float_Volts | uint16 | DC Volts | GSconfig_DC_Voltage_SF | Programmable | Float Voltage Target
64116 | 14 | 14 | 1 | R/W | GSconfig_Float_Time_Hours | uint16 | Hours | GSconfig_Time_SF | Programmable | Float Time Hours
64116 | 15 | 15 | 1 | R/W | GSconfig_ReFloat_Volts | uint16 | DC Volts | GSconfig_DC_Voltage_SF | Programmable | ReFloat Voltage Target
64116 | 16 | 16 | 1 | R/W | GSconfig_EQ_Volts | uint16 | DC Volts | GSconfig_DC_Voltage_SF | Programmable | EQ Voltage Target
64116 | 17 | 17 | 1 | R/W | GSconfig_EQ_Time_Hours | uint16 | Hours | GSconfig_Time_SF | Programmable | EQ Time Hours
64116 | 18 | 18 | 1 | R/W | GSconfig_Search_Sensitivity | uint16 | N/A | N/A | Programmable | Search sensitivity
64116 | 19 | 19 | 1 | R/W | GSconfig_Search_Pulse_Length | uint16 | Cycles | N/A | Programmable | Search pulse length
64116 | 20 | 20 | 1 | R/W | GSconfig_Search_Pulse_Spacing | uint16 | Cycles | N/A | Programmable | Search pulse spacing
64116 | 21 | 21 | 1 | R/W | GSconfig_AC_Input_Select_Priority | uint16 | Enumerated | N/A | Programmable | 0=Grid, 1=Gen
64116 | 22 | 22 | 1 | R/W | GSconfig_Grid_AC_Input_Current_Limit | uint16 | Amps | GSconfig_AC_Current_SF | Programmable | Grid AC input current limit
64116 | 23 | 23 | 1 | R/W | GSconfig_Gen_AC_Input_Current_Limit | uint16 | Amps | GSconfig_AC_Current_SF | Programmable | Gen AC input current limit
64116 | 24 | 24 | 1 | R/W | GSconfig_Charger_AC_Input_Current_Limit | uint16 | Amps | GSconfig_AC_Current_SF | Programmable | Charger AC input current limit
64116 | 25 | 25 | 1 | R/W | GSconfig_Charger_Operating_Mode | uint16 | Enumerated | N/A | Programmable | 0=All Inverter Charging Disabled, 1=Bulk and Float Charging Enabled
64116 | 26 | 26 | 1 | R | GSconfig_AC_Coupled | uint16 | Enumerated | N/A | Programmable | 0=No, 1=Yes
64116 | 27 | 27 | 1 | R/W | GSconfig_Grid_Input_Mode | uint16 | Enumerated | N/A | Programmable | Grid Input Mode: 0=Generator, 1=Support, 2=Grid Tied, 3=UPS, 4=Backup, 5=Mini Grid, 6=Grid Zero
64116 | 28 | 28 | 1 | R/W | GSconfig_Grid_Lower_Input_Voltage_Limit | uint16 | Volts AC | GSconfig_AC_Voltage_SF | Programmable | Grid Input AC voltage lower limit
64116 | 29 | 29 | 1 | R/W | GSconfig_Grid_Upper_Input_Voltage_Limit | uint16 | Volts AC | GSconfig_AC_Voltage_SF | Programmable | Grid Input AC voltage upper limit
64116 | 30 | 30 | 1 | R/W | GSconfig_Grid_Transfer_Delay | uint16 | msecs | N/A | Programmable | Grid Input AC transfer delay
64116 | 31 | 31 | 1 | R/W | GSconfig_Grid_Connect_Delay | uint16 | Minutes | GSconfig_Time_SF | Programmable | Grid Input AC connect delay
64116 | 32 | 32 | 1 | R/W | GSconfig_Gen_Input_Mode | uint16 | Enumerated | N/A | Programmable | Grid Input Mode: 0=Generator, 1=Support, 2=Grid Tied, 3=UPS, 4=Backup, 5=Mini Grid, 6=Grid Zero
64116 | 33 | 33 | 1 | R/W | GSconfig_Gen_Lower_Input_Voltage_Limit | uint16 | Volts AC | GSconfig_AC_Voltage_SF | Programmable | Gen Input AC voltage lower limit
64116 | 34 | 34 | 1 | R/W | GSconfig_Gen_Upper_Input_Voltage_Limit | uint16 | Volts AC | GSconfig_AC_Voltage_SF | Programmable | Gen Input AC voltage upper limit
64116 | 35 | 35 | 1 | R/W | GSconfig_Gen_Transfer_Delay | uint16 | msecs | N/A | Programmable | Gen Input AC transfer delay
64116 | 36 | 36 | 1 | R/W | GSconfig_Gen_Connect_Delay | uint16 | Minutes | GSconfig_Time_SF | Programmable | Gen Input AC connect delay
64116 | 37 | 37 | 1 | R/W | GSconfig_AC_Output_Voltage | uint16 | Volts AC | GSconfig_AC_Voltage_SF | Programmable | AC output Voltage
64116 | 38 | 38 | 1 | R/W | GSconfig_Low_Battery_Cut_Out_Voltage | uint16 | DC Volts | GSconfig_DC_Voltage_SF | Programmable | Battery cut-out voltage
64116 | 39 | 39 | 1 | R/W | GSconfig_Low_Battery_Cut_In_Voltage | uint16 | DC Volts | GSconfig_DC_Voltage_SF | Programmable | Battery cut-in voltage
64116 | 40 | 40 | 1 | R/W | GSconfig_AUX_Mode | uint16 | Enumerated | N/A | Programmable | 1=Load Shed, 2=Gen Alert, 3=Fault, 4=Vent Fan, 5=Cool Fan, 6=DC Divert, 7=Grid Limit/IEEE ,8=AC Source Status,9=AC Divert
64116 | 41 | 41 | 1 | R/W | GSconfig_AUX_Control | uint16 | Enumerated | N/A | Programmable | 0 = Off; 1 = Auto; 2 = On
64116 | 42 | 42 | 1 | R/W | GSconfig_AUX_ON_Battery_Voltage | uint16 | DC Volts | GSconfig_DC_Voltage_SF | Programmable | AUX ON battery voltage
64116 | 43 | 43 | 1 | R/W | GSconfig_AUX_ON_Delay_Time | uint16 | Minutes | GSconfig_Time_SF | Programmable | AUX ON Delay
64116 | 44 | 44 | 1 | R/W | GSconfig_AUX_OFF_Battery_Voltage | uint16 | DC Volts | GSconfig_DC_Voltage_SF | Programmable | AUX OFF battery voltage
64116 | 45 | 45 | 1 | R/W | GSconfig_AUX_OFF_Delay_Time | uint16 | Minutes | GSconfig_Time_SF | Programmable | AUX OFF Delay
64116 | 46 | 46 | 1 | R/W | GSconfig_AUX_Relay_Mode | uint16 | Enumerated | N/A | Programmable | 1=Load Shed, 2=Gen Alert, 3=Fault, 4=Vent Fan, 5=Cool Fan, 6=DC Divert, 7=Grid Limit/IEEE ,8=AC Source Status,9=AC Divert
64116 | 47 | 47 | 1 | R/W | GSconfig_AUX_Relay_Control | uint16 | Enumerated | N/A | Programmable | 0 = Off; 1 = On; 2 = Auto
64116 | 48 | 48 | 1 | R/W | GSconfig_AUX_Relay_ON_Battery_Voltage | uint16 | DC Volts | GSconfig_DC_Voltage_SF | Programmable | AUX Relay ON battery voltage
64116 | 49 | 49 | 1 | R/W | GSconfig_AUX_Relay_ON_Delay_Time | uint16 | Minutes | GSconfig_Time_SF | Programmable | AUX Relay ON Delay
64116 | 50 | 50 | 1 | R/W | GSconfig_AUX_Relay_OFF_Battery_Voltage | uint16 | DC Volts | GSconfig_DC_Voltage_SF | Programmable | AUX Relay OFF battery voltage
64116 | 51 | 51 | 1 | R/W | GSconfig_AUX_Relay_OFF_Delay_Time | uint16 | Minutes | GSconfig_Time_SF | Programmable | AUX Relay OFF Delay
64116 | 52 | 52 | 1 | R/W | GSconfig_Stacking_Mode | uint16 | Enumerated | N/A | Read Only | 10=Master, 12=Slave, 17=B Phase Master, 18=C Phase Master
64116 | 53 | 53 | 1 | R/W | GSconfig_Master_Power_Save_Level | uint16 | N/A | N/A | Programmable | Master inverter power save level
64116 | 54 | 54 | 1 | R/W | GSconfig_Slave_Power_Save_Level | uint16 | N/A | N/A | Programmable | Slave inverter power save level
64116 | 55 | 55 | 1 | R/W | GSconfig_Sell_Volts | uint16 | DC Volts | GSconfig_DC_Voltage_SF | Programmable | Sell Voltage Target
64116 | 56 | 56 | 1 | R/W | GSconfig_Grid_Tie_Window | uint16 | Enumerated | N/A | Programmable | 0=IEEE, 1=User (GS8048 Only)
64116 | 57 | 57 | 1 | R/W | GSconfig_Grid_Tie_Enable | uint16 | Enumerated | N/A | Programmable | 1=Yes, 0=No
64116 | 58 | 58 | 1 | R/W | GSconfig_Grid_AC_Input_Voltage_Calibrate_Factor | int16 | Volts AC | N/A | Programmable | Grid AC input voltage calibration factor
64116 | 59 | 59 | 1 | R/W | GSconfig_Gen_AC_Input_Voltage_Calibrate_Factor | int16 | Volts AC | N/A | Programmable | Gen AC input voltage calibration factor
64116 | 60 | 59 | 1 | R/W | GSconfig_AC_Output_Voltage_Calibrate_Factor | int16 | Volts AC | N/A | Programmable | AC output voltage calibration factor
64116 | 61 | 60 | 1 | R/W | GSconfig_Battery_Voltage_Calibrate_Factor | int16 | DC Volts | GSconfig_DC_Voltage_SF | Programmable | Battery voltage calibration factor
64116 | 62 | 61 | 1 | R/W | GSconfig_ReBulk_Volts | uint16 | DC Volts | GSconfig_DC_Voltage_SF | Programmable | ReBulk Voltage Target
64116 | 63 | 62 | 1 | R/W | GSconfig_Mini_Grid_LBX_Volts | uint16 | DC Volts | GSconfig_DC_Voltage_SF | Programmable | Mini Grid LBX reconnect to Grid Battery Voltage
64116 | 64 | 63 | 1 | R/W | GSconfig_Mini_Grid_LBX_Delay | uint16 | Hours | N/A | Programmable | Mini Grid LBX reconnect to Grid Delay Time
64116 | 65 | 64 | 1 | R/W | GSconfig_Grid_Zero_DoD_Volts | uint16 | DC Volts | GSconfig_DC_Voltage_SF | Programmable | Grid Zero DoD Voltage
64116 | 66 | 65 | 1 | R/W | GSconfig_Grid_Zero_DoD_Max_Offset_AC_Amps | uint16 | Amps | GSconfig_AC_Current_SF | Programmable | Grid Zero Maximum Offset AC Amps
64116 | 67 | 75 | 9 | R | GSconfig_Serial_Number | string (18) | N/A | N/A | Read Only | Device serial number
64116 | 76 | 84 | 9 | R | GSconfig_Model_Number | string (18) | N/A | N/A | Read Only | Device model
64116 | 85 | 85 | 1 | R/W | GSconfig_Module_Control | uint16 | Enumerated | N/A | Programmable | 0=Auto, 1=Left, 2=Right, 3=Both
64116 | 86 | 86 | 1 | R/W | GSconfig_Model_Select | uint16 | Enumerated | N/A | Programmable | 0=Full, 1=Half
64116 | 87 | 87 | 1 | R/W | GSconfig_Low_Battery_Cut_Out_Delay | uint16 | Seconds xx.x | GSconfig_DC_Voltage_SF | Programmable | Low Battery Cut Out Delay
64116 | 88 | 88 | 1 | R/W | GSconfig_High_Battery_Cut_Out_Voltage | uint16 | DC Volts | GSconfig_DC_Voltage_SF | Programmable | High Battery Cut Out Voltage
64116 | 89 | 89 | 1 | R/W | GSconfig_High_Battery_Cut_In_Voltage | uint16 | DC Volts | GSconfig_DC_Voltage_SF | Programmable | High Battery Cut In Voltage
64116 | 90 | 90 | 1 | R/W | GSconfig_High_Battery_Cut_Out_Delay | uint16 | Seconds xx.x | GSconfig_DC_Voltage_SF | Programmable | High Battery Cut Out Delay
64116 | 91 | 91 | 1 | R/W | GSconfig_EE_Write_Enable | uint16 | Enumerated | N/A | Programmable | EEPROM Write Enable 1= Enable, 0= Disable
89
Table 6 Single Phase Radian Inverter Real Time Block
DID | Start | End | Size | R/W | Name | Type | Units | Scale Factor | Contents | Description
64117 | 1 | 1 | 1 | R | GS_Single_DID | uint16 | N/A | N/A | 64117 | Vendor Extension for OutBack Radian Series Split Phase Inverter Status Block
64117 | 2 | 2 | 1 | R | GS_Single_Length | uint16 | Registers | N/A | 47 | Length of block in 16-bit registers
64117 | 3 | 3 | 1 | R | GS_Single_Port_number | uint16 | N/A | N/A | 0-10 | Port number on Outback network
64117 | 4 | 4 | 1 | R | GS_Single_DC_Voltage_SF | int16 | N/A | N/A | -1 | DC Voltage Scale Factor
64117 | 5 | 5 | 1 | R | GS_Single_AC_Current_SF | int16 | N/A | N/A | 0 | AC Current Scale Factor
64117 | 6 | 6 | 1 | R | GS_Single_AC_Voltage_SF | int16 | N/A | N/A | 0 | AC Voltage Scale Factor
64117 | 7 | 7 | 1 | R | GS_Single_AC_Frequency_SF | int16 | N/A | N/A | -1 | AC Frequency Scale Factor
64117 | 8 | 8 | 1 | R | GS_Single_Inverter_Output_Current | uint16 | Amps | GS_Single_AC_Current_SF | Measured | Inverter output current
64117 | 9 | 9 | 1 | R | GS_Single_Inverter_Charge_Current | uint16 | Amps | GS_Single_AC_Current_SF | Measured | Inverter charger current
64117 | 10 | 10 | 1 | R | GS_Single_Inverter_Buy_Current | uint16 | Amps | GS_Single_AC_Current_SF | Measured | Inverter buy current
64117 | 11 | 11 | 1 | R | GS_Single_Inverter_Sell_Current | uint16 | Amps | GS_Single_AC_Current_SF | Measured | Inverter sell current
64117 | 12 | 12 | 1 | R | GS_Single_Grid_Input_AC_Voltage | uint16 | Volts AC | GS_Single_AC_Voltage_SF | Measured | Grid Input AC Voltage
64117 | 13 | 13 | 1 | R | GS_Single_Gen_Input_AC_Voltage | uint16 | Volts AC | GS_Single_AC_Voltage_SF | Measured | Gen Input AC Voltage
64117 | 14 | 14 | 1 | R | GS_Single_Output_AC_Voltage | uint16 | Volts AC | GS_Single_AC_Voltage_SF | Measured | Output AC Voltage
64117 | 15 | 15 | 1 | R | GS_Single_Inverter_Operating_mode | uint16 | Enumerated | N/A | Read Only | 0=Off, 1=Searching, 2=Inverting, 3=Charging, 4=Silent, 5=Float, 6=EQ, 7=Charger Off, 8=Support, 9=Selling, 10=Pass through, 14=Offsetting
64117 | 16 | 16 | 1 | R | GS_Single_Error_Flags | uint16 | Bitfield | N/A | Read Only | Bit field for errors. See GS_Error Table
64117 | 17 | 17 | 1 | R | GS_Single_Warning_Flags | uint16 | Bitfield | N/A | Read Only | Bit field for warnings See GS_Warning Table
64117 | 18 | 18 | 1 | R | GS_Single_Battery_Voltage | uint16 | Volts DC | GS_Single_DC_Voltage_SF | Measured | Battery Voltage
64117 | 19 | 19 | 1 | R | GS_Single_Temp_Compensated_Target_Voltage | uint16 | Volts DC | GS_Single_DC_Voltage_SF | Read Only | Temperature compensated target battery voltage
64117 | 20 | 20 | 1 | R | GS_Single_AUX_Output_State | uint16 | Enumerated | N/A | Read Only | 0 = Disabled; 1 = Enabled
64117 | 21 | 21 | 1 | R | GS_Single_AUX_Relay_Output_State | uint16 | Enumerated | N/A | Read Only | 0 = Disabled; 1 = Enabled
64117 | 22 | 22 | 1 | R | GS_Single_L_Module_Transformer_Temperature | int16 | Degrees C | N/A | Measured | Left module transformer temp in degrees C
64117 | 23 | 23 | 1 | R | GS_Single_L_Module_Capacitor_Temperature | int16 | Degrees C | N/A | Measured | Left module capacitor temp in degrees C
64117 | 24 | 24 | 1 | R | GS_Single_L_Module_FET_Temperature | int16 | Degrees C | N/A | Measured | Left module FET temp in degrees C
64117 | 25 | 25 | 1 | R | GS_Single_R_Module_Transformer_Temperature | int16 | Degrees C | N/A | Measured | Right module transformer temp in degrees C
64117 | 26 | 26 | 1 | R | GS_Single_R_Module_Capacitor_Temperature | int16 | Degrees C | N/A | Measured | Right module capacitor temp in degrees C
64117 | 27 | 27 | 1 | R | GS_Single_R_Module_FET_Temperature | int16 | Degrees C | N/A | Measured | Right module FET temp in degrees C
64117 | 28 | 28 | 1 | R | GS_Single_Battery_Temperature | int16 | Degrees C | N/A | Measured | Battery temp in degrees C
64117 | 29 | 29 | 1 | R | GS_Single_AC_Input_Selection | uint16 | Enumerated | N/A | Read Only | 0=Grid, 1=Gen
64117 | 30 | 30 | 1 | R | GS_Single_AC_Input_Frequency | uint16 | Hz | GS_Single_AC_Frequency_SF | Measured | Selected AC Input frequency HZ
64117 | 31 | 31 | 1 | R | GS_Single_AC_Input_Voltage | uint16 | Volts AC | GS_Single_AC_Voltage_SF | Measured | Selected Input AC Voltage
64117 | 32 | 32 | 1 | R | GS_Single_AC_Input_State | uint16 | Enumerated | N/A | N/A | 1=AC Use, 0=AC_Drop
64117 | 33 | 33 | 1 | R | GS_Single_Minimum_AC_Input_Voltage | uint16 | Volts AC | GS_Single_AC_Voltage_SF | Read Only | Minimum Input AC Voltage (Write to clear value)
64117 | 34 | 34 | 1 | R | GS_Single_Maximum_AC_Input_Voltage | uint16 | Volts AC | GS_Single_AC_Voltage_SF | Read Only | Maximum Input AC Voltage (Write to clear value)
64117 | 35 | 35 | 1 | R | GS_Single_Sell_Status | uint16 | Bitfield | N/A | N/A | Bit field for sell status See GS_Sell_Status Table
64117 | 36 | 36 | 1 | R | GS_Single_kWh_SF | int16 | N/A | N/A | -1 | AC kWh scale factor
64117 | 37 | 37 | 1 | R | GS_Single_AC1_Buy_kWh | uint16 | kWh | GS_Single_kWh_SF | Measured | Daily AC1 Buy kWh
64117 | 38 | 38 | 1 | R | GS_Single_AC2_Buy_kWh | uint16 | kWh | GS_Single_kWh_SF | Measured | Daily AC2 Buy kWh
64117 | 39 | 39 | 1 | R | GS_Single_AC1_Sell_kWh | uint16 | kWh | GS_Single_kWh_SF | Measured | Daily AC1 Sell kWh
64117 | 40 | 40 | 1 | R | GS_Single_AC2_Sell_kWh | uint16 | kWh | GS_Single_kWh_SF | Measured | Daily AC2 Sell kWh
64117 | 41 | 41 | 1 | R | GS_Single_Output_kWh | uint16 | kWh | GS_Single_kWh_SF | Measured | Daily Output kWh
64117 | 42 | 42 | 1 | R | GS_Single_Charger_kWh | uint16 | kWh | GS_Single_kWh_SF | Measured | Daily Charger kWh
64117 | 43 | 43 | 1 | R | GS_Single_Output_kW | uint16 | kW | GS_Single_kWh_SF | Measured | Output kW
64117 | 44 | 44 | 1 | R | GS_Single_Buy_kW | uint16 | kW | GS_Single_kWh_SF | Measured | Buy kW
64117 | 45 | 45 | 1 | R | GS_Single_Sell_kW | uint16 | kW | GS_Single_kWh_SF | Measured | Sell kW
64117 | 46 | 46 | 1 | R | GS_Single_Charge_kW | uint16 | kW | GS_Single_kWh_SF | Measured | Charger kW
64117 | 47 | 47 | 1 | R | GS_Single_Load_kW | uint16 | kW | GS_Single_kWh_SF | Measured | Load kW
64117 | 48 | 48 | 1 | R | GS_Single_AC_Couple_kW | uint16 | kW | GS_Single_kWh_SF | Measured | AC Coupled kW
64117 | 49 | 49 | 1 | R | GS_Single_GT_Number | uint16 | N/A | N/A | Measured | GT Number sent from Inverter to Charge Controller
Table 7 FX Inverter Real Time Block
DID | Start | End | Size | R/W | Name | Type | Units | Scale Factor | Contents | Description
64113 | 1 | 1 | 1 | R | FX_DID | uint16 | N/A | N/A | 64113 | Vendor Extension for OutBack FX Series Inverter Status Block
64113 | 2 | 2 | 1 | R | FX_Length | uint16 | Registers | N/A | 36 | Length of block in 16-bit registers
64113 | 3 | 3 | 1 | R | FX_Port_number | uint16 | N/A | N/A | 0-10 | Port number on Outback network
64113 | 4 | 4 | 1 | R | FX_DC_Voltage_SF | int16 | N/A | N/A | -1 | DC Voltage Scale Factor
64113 | 5 | 5 | 1 | R | FX_AC_Current_SF | int16 | N/A | N/A | 0 | AC Current Scale Factor
64113 | 6 | 6 | 1 | R | FX_AC_Voltage_SF | int16 | N/A | N/A | 0 | AC Voltage Scale Factor
64113 | 7 | 7 | 1 | R | FX_AC_Frequency_SF | int16 | N/A | N/A | -1 | AC Frequency Scale Factor
64113 | 8 | 8 | 1 | R | FX_Inverter_Output_Current | uint16 | Amps | FX_AC_Current_SF | Measured | Inverter output current
64113 | 9 | 9 | 1 | R | FX_Inverter_Charge_Current | uint16 | Amps | FX_AC_Current_SF | Measured | Inverter charger current
64113 | 10 | 10 | 1 | R | FX_Inverter_Buy_Current | uint16 | Amps | FX_AC_Current_SF | Measured | Inverter buy current
64113 | 11 | 11 | 1 | R | FX_Inverter_Sell_Current | uint16 | Amps | FX_AC_Current_SF | Measured | Inverter sell current
64113 | 12 | 12 | 1 | R | FX_Output_AC_Voltage | uint16 | Volts AC | FX_AC_Voltage_SF | Measured | Output AC Voltage
64113 | 13 | 13 | 1 | R | FX_Inverter_Operating_Mode | uint16 | Enumerated | N/A | Read Only | 0=Off, 1=Searching, 2=Inverting, 3=Charging, 4=Silent, 5=Float, 6=EQ, 7=Charger Off, 8=Support, 9=Selling, 10=Pass through, 14=Offsetting
64113 | 14 | 14 | 1 | R | FX_Error_Flags | uint16 | Bitfield | N/A | Read Only | Bit field for errors. See FX_Error Table
64113 | 15 | 15 | 1 | R | FX_Warning_Flags | uint16 | Bitfield | N/A | Read Only | Bit field for warnings See FX_Warning Table
64113 | 16 | 16 | 1 | R | FX_Battery_Voltage | uint16 | Volts DC | FX_DC_Voltage_SF | Measured | Battery Voltage
64113 | 17 | 17 | 1 | R | FX_Temp_Compensated_Target_Voltage | uint16 | Volts DC | FX_DC_Voltage_SF | Read Only | Temperature compensated target battery voltage
64113 | 18 | 18 | 1 | R | FX_AUX_Output_State | uint16 | Enumerated | N/A | Read Only | 0 = Disabled; 1 = Enabled
64113 | 19 | 19 | 1 | R | FX_Transformer_Temperature | int16 | Degrees C | N/A | Measured | Transformer temp in degrees C
64113 | 20 | 20 | 1 | R | FX_Capacitor_Temperature | int16 | Degrees C | N/A | Measured | Capacitor temp in degrees C
64113 | 21 | 21 | 1 | R | FX_FET_Temperature | int16 | Degrees C | N/A | Measured | FET temp in degrees C
64113 | 22 | 22 | 1 | R | FX_AC_Input_Frequency | uint16 | Hz | FX_AC_Frequency_SF | Measured | Selected AC Input frequency HZ
64113 | 23 | 23 | 1 | R | FX_AC_Input_Voltage | uint16 | Volts AC | FX_AC_Voltage_SF | Measured | Selected Input AC Voltage
64113 | 24 | 24 | 1 | R | FX_AC_Input_State | uint16 | Enumerated | N/A | N/A | 1=AC Use, 0=AC_Drop
64113 | 25 | 25 | 1 | R | FX_Minimum_AC_Input_Voltage | uint16 | Volts AC | FX_AC_Voltage_SF | Read Only | Minimum Input AC Voltage (Write to clear value)
64113 | 26 | 26 | 1 | R | FX_Maximum_AC_Input_Voltage | uint16 | Volts AC | FX_AC_Voltage_SF | Read Only | Maximum Input AC Voltage (Write to clear value)
64113 | 27 | 27 | 1 | R | FX_Sell_Status | uint16 | Bitfield | N/A | N/A | Bit field for sell status See FX_Sell_Status Table
64113 | 28 | 28 | 1 | R | FX_kWh_SF | int16 | N/A | N/A | -1 | AC kWh scale factor
64113 | 29 | 29 | 1 | R | FX_Buy_kWh | uint16 | kWh | FX_kWh_SF | Measured | Daily Buy kWh
64113 | 30 | 30 | 1 | R | FX_Sell_kWh | uint16 | kWh | FX_kWh_SF | Measured | Daily Sell kWh
64113 | 31 | 31 | 1 | R | FX_Output_kWh | uint16 | kWh | FX_kWh_SF | Measured | Daily Output kWh
64113 | 32 | 32 | 1 | R | FX_Charger_kWh | uint16 | kWh | FX_kWh_SF | Measured | Daily Charger kWh
64113 | 33 | 33 | 1 | R | FX_Output_kW | uint16 | kW | FX_kWh_SF | Measured | Output kW
64113 | 34 | 34 | 1 | R | FX_Buy_kW | uint16 | kW | FX_kWh_SF | Measured | Buy kW
64113 | 35 | 35 | 1 | R | FX_Sell_kW | uint16 | kW | FX_kWh_SF | Measured | Sell kW
64113 | 36 | 36 | 1 | R | FX_Charge_kW | uint16 | kW | FX_kWh_SF | Measured | Charge kW
64113 | 37 | 37 | 1 | R | FX_Load_kW | uint16 | kW | FX_kWh_SF | Measured | Load kW
64113 | 38 | 38 | 1 | R | FX_AC_Couple_kW | uint16 | kW | FX_kWh_SF | Measured | AC Coupled kW
FX_Error Table
[9 empty] | Contents | Description
[9 empty] | 0x0001 | Low AC output voltage
[9 empty] | 0x0002 | Stacking error
[9 empty] | 0x0004 | Over temperature error
[9 empty] | 0x0008 | Low battery voltage
[9 empty] | 0x0010 | Phase loss
[9 empty] | 0x0020 | High battery voltage
[9 empty] | 0x0040 | AC output shorted
[9 empty] | 0x0080 | AC backfeed
FX_Warning Table
[9 empty] | Contents | Description
[9 empty] | 0x0001 | AC input frequency too high
[9 empty] | 0x0002 | AC input frequency too low
[9 empty] | 0x0004 | AC input voltage too low
[9 empty] | 0x0008 | AC input voltage too high
[9 empty] | 0x0010 | AC input current exceeds max
[9 empty] | 0x0020 | Temperature sensor bad
[9 empty] | 0x0040 | Communications error
[9 empty] | 0x0080 | Cooling fan fault
FX_Sell_Status Table
[9 empty] | Contents | Description
[9 empty] | 0x0001 | AC input frequency too high
[9 empty] | 0x0002 | AC input frequency too low
[9 empty] | 0x0004 | AC input voltage too low
[9 empty] | 0x0008 | AC input voltage too high
[9 empty] | 0x0010 | Awaiting sell delay
[9 empty] | 0x0020 | Sell disabled
[9 empty] | 0x0040 | Battery voltage less than target
[9 empty] | 0x0080 | AC2 selected
Table 8 FX Inverter Configuration Block
DID | Start | End | Size | R/W | Name | Type | Units | Scale Factor | Contents | Description
64114 | 1 | 1 | 1 | R | FXconfig_DID | uint16 | N/A | N/A | 64114 | Vendor Extension for OutBack FX Series Inverter Configuration Block
64114 | 2 | 2 | 1 | R | FXconfig_Length | uint16 | Registers | N/A | 72 | Length of block in 16-bit registers
64114 | 3 | 3 | 1 | R | FXconfig_Port_Number | uint16 | N/A | N/A | 0-10 | Port number on Outback network
64114 | 4 | 4 | 1 | R | FXconfig_DC_Voltage_SF | int16 | N/A | N/A | -1 | DC Voltage Scale Factor
64114 | 5 | 5 | 1 | R | FXconfig_AC_Current_SF | int16 | N/A | N/A | -1 | AC Current Scale Factor
64114 | 6 | 6 | 1 | R | FXconfig_AC_Voltage_SF | int16 | N/A | N/A | 0 | AC Voltage Scale Factor
64114 | 7 | 7 | 1 | R | FXconfig_Time_SF | int16 | N/A | N/A | -1 | Time Scale Factor
64114 | 8 | 8 | 1 | R | FXconfig_Major_Firmware_Number | uint16 | N/A | N/A | Read Only | Inverter Major firmware revision
64114 | 9 | 9 | 1 | R | FXconfig_Mid_Firmware_Number | uint16 | N/A | N/A | Read Only | Inverter Mid firmware revision
64114 | 10 | 10 | 1 | R | FXconfig_Minor_Firmware_Number | uint16 | N/A | N/A | Read Only | Inverter Minor firmware revision
64114 | 11 | 11 | 1 | R/W | FXconfig_Absorb_Volts | uint16 | DC Volts | FXconfig_DC_Voltage_SF | Programmable | Absorb Voltage Target
64114 | 12 | 12 | 1 | R/W | FXconfig_Absorb_Time_Hours | uint16 | Hours | FXconfig_Time_SF | Programmable | Absorb Time Hours
64114 | 13 | 13 | 1 | R/W | FXconfig_Float_Volts | uint16 | DC Volts | FXconfig_DC_Voltage_SF | Programmable | Float Voltage Target
64114 | 14 | 14 | 1 | R/W | FXconfig_Float_Time_Hours | uint16 | Hours | FXconfig_Time_SF | Programmable | Float Time Hours
64114 | 15 | 15 | 1 | R/W | FXconfig_ReFloat_Volts | uint16 | DC Volts | FXconfig_DC_Voltage_SF | Programmable | ReFloat Voltage Target
64114 | 16 | 16 | 1 | R/W | FXconfig_EQ_Volts | uint16 | DC Volts | FXconfig_DC_Voltage_SF | Programmable | EQ Voltage Target
64114 | 17 | 17 | 1 | R/W | FXconfig_EQ_Time_Hours | uint16 | Hours | FXconfig_Time_SF | Programmable | EQ Time Hours
64114 | 18 | 18 | 1 | R/W | FXconfig_Search_Sensitivity | uint16 | N/A | N/A | Programmable | Search sensitivity
64114 | 19 | 19 | 1 | R/W | FXconfig_Search_Pulse_Length | uint16 | Cycles | N/A | Programmable | Search pulse length
64114 | 20 | 20 | 1 | R/W | FXconfig_Search_Pulse_Spacing | uint16 | Cycles | N/A | Programmable | Search pulse spacing
64114 | 21 | 21 | 1 | R/W | FXconfig_AC_Input_Type | uint16 | Enumerated | N/A | Programmable | 0=Grid, 1=Gen, 2=Grid Zero
64114 | 22 | 22 | 1 | R/W | Fxconfig_Input_Support | uint16 | Enumerated | N/A | Programmable | 1=Yes, 0=No (only valid if AC Input Type is Gen)
64114 | 23 | 23 | 1 | R/W | FXconfig_Grid_AC_Input_Current_Limit | uint16 | Amps | FXconfig_AC_Current_SF | Programmable | Grid AC input current limit
64114 | 24 | 24 | 1 | R/W | FXconfig_Gen_AC_Input_Current_Limit | uint16 | Amps | FXconfig_AC_Current_SF | Programmable | Gen AC input current limit
64114 | 25 | 25 | 1 | R/W | FXconfig_Charger_AC_Input_Current_Limit | uint16 | Amps | FXconfig_AC_Current_SF | Programmable | Charger AC input current limit
64114 | 26 | 26 | 1 | R/W | FXconfig_Charger_Operating_Mode | uint16 | Enumerated | N/A | Programmable | 0=Charger Off, 1=Charger Auto, 2=Charger On
64114 | 27 | 27 | 1 | R/W | FXconfig_Grid_Lower_Input_Voltage_Limit | uint16 | Volts AC | FXconfig_AC_Voltage_SF | Programmable | Grid Input AC voltage lower limit
64114 | 28 | 28 | 1 | R/W | FXconfig_Grid_Upper_Input_Voltage_Limit | uint16 | Volts AC | FXconfig_AC_Voltage_SF | Programmable | Grid Input AC voltage upper limit
64114 | 29 | 29 | 1 | R/W | FXconfig_Grid_Transfer_Delay | uint16 | Minutes | N/A | Programmable | Grid Input AC connect delay
64114 | 30 | 30 | 1 | R/W | FXconfig_Gen_Lower_Input_Voltage_Limit | uint16 | Volts AC | FXconfig_AC_Voltage_SF | Programmable | Gen Input AC voltage lower limit
64114 | 31 | 31 | 1 | R/W | FXconfig_Gen_Upper_Input_Voltage_Limit | uint16 | Volts AC | FXconfig_AC_Voltage_SF | Programmable | Gen Input AC voltage upper limit
64114 | 32 | 32 | 1 | R/W | FXconfig_Gen_Transfer_Delay | uint16 | Cycles | N/A | Programmable | Gen Input AC transfer delay
64114 | 33 | 33 | 1 | R/W | FXconfig_Gen_Connect_Delay | uint16 | Minutes | FXconfig_Time_SF | Programmable | Gen Input AC connect delay
64114 | 34 | 34 | 1 | R/W | FXconfig_AC_Output_Voltage | uint16 | Volts AC | FXconfig_AC_Voltage_SF | Programmable | AC output Voltage
64114 | 35 | 35 | 1 | R/W | FXconfig_Low_Battery_Cut_Out_Voltage | uint16 | DC Volts | FXconfig_DC_Voltage_SF | Programmable | Battery cut-out voltage
64114 | 36 | 36 | 1 | R/W | FXconfig_Low_Battery_Cut_In_Voltage | uint16 | DC Volts | FXconfig_DC_Voltage_SF | Programmable | Battery cut-in voltage
64114 | 37 | 37 | 1 | R/W | FXconfig_AUX_Mode | uint16 | Enumerated | N/A | Programmable | 0=Remote, 1=Load Shed, 2=Gen Alert, 3=Fault, 4=Vent Fan, 5=Cool Fan, 6=Divert DC, 7=Divert AC, 8=AC Drop
64114 | 38 | 38 | 1 | R/W | FXconfig_AUX_Control | uint16 | Enumerated | N/A | Programmable | 0 = Off; 1 = Auto; 2 = On
64114 | 39 | 39 | 1 | R/W | FXconfig_AUX_Load_Shed_Enable_Voltage | uint16 | DC Volts | FXconfig_DC_Voltage_SF | Programmable | Load Shed enable voltage
64114 | 40 | 40 | 1 | R/W | FXconfig_AUX_Gen_Alert_On_Voltage | uint16 | DC Volts | FXconfig_DC_Voltage_SF | Programmable | Gen Alert On voltage
64114 | 41 | 41 | 1 | R/W | FXconfig_AUX_Gen_Alert_On_Delay | uint16 | Minutes | N/A | Programmable | Gen Alert On delay minutes
64114 | 42 | 42 | 1 | R/W | FXconfig_AUX_Gen_Alert_Off_Voltage | uint16 | DC Volts | FXconfig_DC_Voltage_SF | Programmable | Gen Alert Off voltage
64114 | 43 | 43 | 1 | R/W | FXconfig_AUX_Gen_Alert_Off_Delay | uint16 | Minutes | N/A | Programmable | Gen Alert Off delay minutes
64114 | 44 | 44 | 1 | R/W | FXconfig_AUX_Vent_Fan_Enable_Voltage | uint16 | DC Volts | FXconfig_DC_Voltage_SF | Programmable | Vent Fan enable voltage
64114 | 45 | 45 | 1 | R/W | FXconfig_AUX_Vent_Fan_Off_Period | uint16 | Minutes | N/A | Programmable | Van Fan Off delay minutes
64114 | 46 | 46 | 1 | R/W | FXconfig_AUX_Divert_Enable_Voltage | uint16 | DC Volts | FXconfig_DC_Voltage_SF | Programmable | DC Divert enable voltage
64114 | 47 | 47 | 1 | R/W | FXconfig_AUX_Divert_Off_Delay | uint16 | Minutes | N/A | Programmable | Divert Off delay minutes
64114 | 48 | 48 | 1 | R/W | FXconfig_Stacking_Mode | uint16 | Enumerated | N/A | Read Only | 0=1-2phase Master, 1=Classic Slave, 2=OB Slave L1, 3=OB Slave L2, 4=3phase Master, 5=3phase Slave,10=Master, 11=Classic Slave, 12=OB Slave L1, 13=OB Slave L2, 14=3phase OB Slave A, 15=3phase OB Slave B, 16=3phase OB Slave C, 17=3phase Classic B, 18=3phase Classic C, 19=Independent
64114 | 49 | 49 | 1 | R/W | FXconfig_Master_Power_Save_Level | uint16 | N/A | N/A | Programmable | Master inverter power save level
64114 | 50 | 50 | 1 | R/W | FXconfig_Slave_Power_Save_Level | uint16 | N/A | N/A | Programmable | Slave inverter power save level
64114 | 51 | 51 | 1 | R/W | FXconfig_Sell_Volts | uint16 | DC Volts | FXconfig_DC_Voltage_SF | Programmable | Sell Voltage Target
64114 | 52 | 52 | 1 | R/W | FXconfig_Grid_Tie_Window | uint16 | Enumerated | N/A | Programmable | 0=IEEE, 1=User
64114 | 53 | 53 | 1 | R/W | FXconfig_Grid_Tie_Enable | uint16 | Enumerated | N/A | Programmable | 1=Yes, 0=No
64114 | 54 | 54 | 1 | R/W | FXconfig_AC_Input_Voltage_Calibrate_Factor | int16 | Volts AC | N/A | Programmable | AC input voltage calibration factor
64114 | 55 | 55 | 1 | R/W | FXconfig_AC_Output_Voltage_Calibrate_Factor | int16 | Volts AC | N/A | Programmable | AC output voltage calibration factor
64114 | 56 | 56 | 1 | R/W | FXconfig_Battery_Voltage_Calibrate_Factor | int16 | DC Volts | FXconfig_DC_Voltage_SF | Programmable | Battery voltage calibration factor
64114 | 57 | 65 | 9 | R | FXconfig_Serial_Number | string (18) | N/A | N/A | Read Only | Device serial number
64114 | 66 | 74 | 9 | R | FXconfig_Model_Number | string (18) | N/A | N/A | Read Only | Device model
Table 9 FLEXnet-DC Configuration Block
DID | Start | End | Size | R/W | Name | Type | Units | Scale Factor | Contents | Description
64119 | 1 | 1 | 1 | R | FNconfig_DID | uint16 | N/A | N/A | 64119 | Vendor Extension for OutBack FLEXnet-DC Battery Monitor Configuration Block
64119 | 2 | 2 | 1 | R | FNconfig_Length | uint16 | Registers | N/A | 52 | Length of block in 16-bit registers
64119 | 3 | 3 | 1 | R | FNconfig_Port_Number | uint16 | N/A | N/A | 1-10 | Port number on OutBack network
64119 | 4 | 4 | 1 | R | FNconfig_DC_Voltage_SF | int16 | N/A | N/A | -1 | DC Voltage Scale Factor
64119 | 5 | 5 | 1 | R | FNconfig_DC_Current_SF | int16 | N/A | N/A | -1 | DC Current Scale Factor
64119 | 6 | 6 | 1 | R | FNconfig_kWh_SF | int16 | N/A | N/A | -2 | Kilo Watt Hours Scale Factor
64119 | 7 | 7 | 1 | R | FNconfig_Major_Firmware_Number | uint16 | N/A | N/A | Read Only | FLEXnet-DC Major firmware revision
64119 | 8 | 8 | 1 | R | FNconfig_Mid_Firmware_Number | uint16 | N/A | N/A | Read Only | FLEXnet-DC Mid firmware revision
64119 | 9 | 9 | 1 | R | FNconfig_Minor_Firmware_Number | uint16 | N/A | N/A | Read Only | FLEXnet-DC Minor firmware revision
64119 | 10 | 10 | 1 | R/W | FNconfig_Battery_Capacity | uint16 | AH | N/A | Programmable | Battery AH capacity
64119 | 11 | 11 | 1 | R/W | FNconfig_Charged_Volts | uint16 | DC Volts | FNconfig_DC_Voltage_SF | Programmable | Battery Charged Voltage
64119 | 12 | 12 | 1 | R/W | FNconfig_Charged_Time | uint16 | Minutes | N/A | Programmable | Battery Charged Time Minutes
64119 | 13 | 13 | 1 | R/W | FNconfig_Battery_Charged_Amps | uint16 | Amps | FNconfig_DC_Current_SF | Programmable | Battery Charged Return Amps
64119 | 14 | 14 | 1 | R/W | FNconfig_Charge_Factor | uint16 | Percent | N/A | Programmable | Battery Charge Factor
64119 | 15 | 15 | 1 | R/W | FNconfig_Shunt_A_Enabled | uint16 | Enumerated | N/A | Programmable | 0=Enabled, 1=Disabled
64119 | 16 | 16 | 1 | R/W | FNconfig_Shunt_B_Enabled | uint16 | Enumerated | N/A | Programmable | 0=Enabled, 1=Disabled
64119 | 17 | 17 | 1 | R/W | FNconfig_Shunt_C_Enabled | uint16 | Enumerated | N/A | Programmable | 0=Enabled, 1=Disabled
64119 | 18 | 18 | 1 | R/W | FNconfig_Relay_Control | uint16 | Enumerated | N/A | Programmable | 0 = Off; 1 = Auto; 2 = On
64119 | 19 | 19 | 1 | R/W | FNconfig_Relay_Invert_Logic | uint16 | Enumerated | N/A | Programmable | 0=Invert Logic,1=Normal
64119 | 20 | 20 | 1 | R/W | FNconfig_Relay_High_Voltage | uint16 | DC Volts | FNconfig_DC_Voltage_SF | Programmable | Relay high voltage enable
64119 | 21 | 21 | 1 | R/W | FNconfig_Relay_Low_Voltage | uint16 | DC Volts | FNconfig_DC_Voltage_SF | Programmable | Relay low voltage enable
64119 | 22 | 22 | 1 | R/W | FNconfig_Relay_SOC_High | uint16 | Percent | N/A | Programmable | Relay high SOC enable
64119 | 23 | 23 | 1 | R/W | FNconfig_Relay_SOC_Low | uint16 | Percent | N/A | Programmable | Relay low SOC enable
64119 | 24 | 24 | 1 | R/W | FNconfig_Relay_High_Enable_Delay | uint16 | Minutes | N/A | Programmable | Relay High Enable Delay
64119 | 25 | 25 | 1 | R/W | FNconfig_Relay_Low_Enable_Delay | uint16 | Minutes | N/A | Programmable | Relay Low Enable Delay
64119 | 26 | 26 | 1 | R/W | FNconfig_Set_Data_Log_Day_Offset | uint16 | Days | N/A | Programmable | Day offset 0-400, 0 =Today, 1 = -1 day …
64119 | 27 | 27 | 1 | R | FNconfig_Get_Current_Data_Log_Day_Offset | uint16 | Days | N/A | Read Only | Current Data Log Day Offset
64119 | 28 | 28 | 1 | R | FNconfig_Datalog_Minimum_SOC | uint16 | Percent | N/A | Read Only | Datalog minimum SOC
64119 | 29 | 29 | 1 | R | FNconfig_Datalog_Input_AH | uint16 | AH | N/A | Read Only | Datalog input AH
64119 | 30 | 30 | 1 | R | FNconfig_Datalog_Input_kWh | uint16 | kWh | FNconfig_kWh_SF | Read Only | Datalog input kWh
64119 | 31 | 31 | 1 | R | FNconfig_Datalog_Output_AH | uint16 | AH | N/A | Read Only | Datalog output AH
64119 | 32 | 32 | 1 | R | FNconfig_Datalog_Output_kWh | uint16 | kWh | FNconfig_kWh_SF | Read Only | Datalog output kWh
64119 | 33 | 33 | 1 | R | FNconfig_Datalog_NET_AH | uint16 | AH | N/A | Read Only | Datalog NET AH
64119 | 34 | 34 | 1 | R | FNconfig_Datalog_NET_kWh | uint16 | kWh | FNconfig_kWh_SF | Read Only | Datalog NET kWh
64119 | 35 | 35 | 1 | R | FNconfig_Clear_Data_Log_Read | uint16 | N/A | N/A | Read Only | Read value needed to clear data log
64119 | 36 | 36 | 1 | W | FNconfig_Clear_Data_Log_Write_Complement | uint16 | N/A | N/A | Write Only | Write value's complement to clear data log
64119 | 37 | 45 | 9 | R | FNconfig_Serial_Number | string (18) | N/A | N/A | Read Only | Device serial number
64119 | 46 | 54 | 9 | R | FNconfig_Model_Number | string (18) | N/A | N/A | Read Only | Device model
Table 10 FLEXnet-DC Real Time Block
DID | Start | End | Size | R/W | Name | Type | Units | Scale Factor | Contents | Description
64118 | 1 | 1 | 1 | R | FN_DID | uint16 | N/A | N/A | 64118 | Vendor Extension for OutBack FLEXnet DC Battery Monitor Status Block
64118 | 2 | 2 | 1 | R | FN_Length | uint16 | Registers | N/A | 76 | Length of block in 16-bit registers
64118 | 3 | 3 | 1 | R | FN_Port_Number | uint16 | N/A | N/A | 1-10 | Port number on Outback network
64118 | 4 | 4 | 1 | R | FN_DC_Voltage_SF | int16 | N/A | N/A | -1 | DC Voltage Scale Factor
64118 | 5 | 5 | 1 | R | FN_DC_Current_SF | int16 | N/A | N/A | -1 | DC Current Scale Factor
64118 | 6 | 6 | 1 | R | FN_Time_SF | int16 | N/A | N/A | -1 | Time Scale Factor
64118 | 7 | 7 | 1 | R | FN_kWh_SF | int16 | N/A | N/A | -2 | Kilo Watt Hours Scale Factor
64118 | 8 | 8 | 1 | R | FN_kW_SF | int16 | N/A | N/A | -2 | Kilo Watt Scale Factor
64118 | 9 | 9 | 1 | R | FN_Shunt_A_Current | int16 | Amps | FN_DC_Current_SF | Read Only | Shunt A current
64118 | 10 | 10 | 1 | R | FN_Shunt_B_Current | int16 | Amps | FN_DC_Current_SF | Read Only | Shunt B current
64118 | 11 | 11 | 1 | R | FN_Shunt_C_Current | int16 | Amps | FN_DC_Current_SF | Read Only | Shunt C current
64118 | 12 | 12 | 1 | R | FN_Battery_Voltage | uint16 | Volts | FN_DC_Voltage_SF | Read Only | Battery Voltage
64118 | 13 | 13 | 1 | R | FN_Battery_Current | int16 | Amps | FN_DC_Current_SF | Read Only | Battery Current
64118 | 14 | 14 | 1 | R | FN_Battery_Temperature | int16 | Degrees C | N/A | Read Only | Battery Temperature C
64118 | 15 | 15 | 1 | R | FN_Status_Flags | uint16 | Bitfield | N/A | Read Only | See FN Status Table
64118 | 16 | 16 | 1 | R | FN_Shunt_A_Accumulated_AH | int16 | AH | N/A | Read Only | Shunt A Accumulated_AH
64118 | 17 | 17 | 1 | R | FN_Shunt_A_Accumulated_kWh | int16 | kWh | FN_kWh_SF | Read Only | Shunt A Accumulated_kWh
64118 | 18 | 18 | 1 | R | FN_Shunt_B_Accumulated_AH | int16 | AH | N/A | Read Only | Shunt B Accumulated_AH
64118 | 19 | 19 | 1 | R | FN_Shunt_B_Accumulated_kWh | int16 | kWh | FN_kWh_SF | Read Only | Shunt B Accumulated_kWh
64118 | 20 | 20 | 1 | R | FN_Shunt_C_Accumulated_AH | int16 | AH | N/A | Read Only | Shunt C Accumulated_AH
64118 | 21 | 21 | 1 | R | FN_Shunt_C_Accumulated_kWh | int16 | kWh | FN_kWh_SF | Read Only | Shunt C Accumulated_kWh
64118 | 22 | 22 | 1 | R | FN_Input_Current | uint16 | Amps | FN_DC_Current_SF | Read Only | Total_input_current
64118 | 23 | 23 | 1 | R | FN_Output_Current | uint16 | Amps | FN_DC_Current_SF | Read Only | Total_output_current
64118 | 24 | 24 | 1 | R | FN_Input_kW | uint16 | kW | FN_kW_SF | Read Only | Total_input_kWatts
64118 | 25 | 25 | 1 | R | FN_Output_kW | uint16 | kW | FN_kW_SF | Read Only | Total_output_kWatts
64118 | 26 | 26 | 1 | R | FN_Net_kW | int16 | kW | FN_kW_SF | Read Only | Total_net_kWatts
64118 | 27 | 27 | 1 | R | FN_Days_Since_Charge_Parameters_Met | uint16 | Days | FN_Time_SF | Read Only | Days Since Charge Parameters Met
64118 | 28 | 28 | 1 | R | FN_State_Of_Charge | uint16 | Percent | N/A | Read Only | Current Battery State of Charge
64118 | 29 | 29 | 1 | R | FN_Todays_Minimum_SOC | uint16 | Percent | N/A | Read Only | Todays minimum SOC
64118 | 30 | 30 | 1 | R | FN_Todays_Maximum_SOC | uint16 | Percent | N/A | Read Only | Todays maximum SOC
64118 | 31 | 31 | 1 | R | FN_Todays_NET_Input_AH | uint16 | AH | N/A | Read Only | Todays NET input AH
64118 | 32 | 32 | 1 | R | FN_Todays_NET_Input_kWh | uint16 | kWh | FN_kWh_SF | Read Only | Todays NET input kWh
64118 | 33 | 33 | 1 | R | FN_Todays_NET_Output_AH | uint16 | AH | N/A | Read Only | Todays NET output AH
64118 | 34 | 34 | 1 | R | FN_Todays_NET_Output_kWh | uint16 | kWh | FN_kWh_SF | Read Only | Todays NET output kWh
64118 | 35 | 35 | 1 | R | FN_Todays_NET_Battery_AH | int16 | AH | N/A | Read Only | Todays NET battery AH
64118 | 36 | 36 | 1 | R | FN_Todays_NET_Battery_kWh | int16 | kWh | FN_kWh_SF | Read Only | Todays NET battery kWh
64118 | 37 | 37 | 1 | R | FN_Charge_Factor_Corrected_NET_Battery_AH | int16 | AH | N/A | Read Only | Charge factor corrected NET battery AH
64118 | 38 | 38 | 1 | R | FN_Charge_Factor_Corrected_NET_Battery_kWh | int16 | kWh | FN_kWh_SF | Read Only | Charge factor corrected NET battery kWh
64118 | 39 | 39 | 1 | R | FN_Todays_Minimum_Battery_Voltage | uint16 | Volts | FN_DC_Voltage_SF | Programmable | Todays minimum battery voltage
64118 | 40 | 41 | 2 | R | FN_Todays_Minimum_Battery_Time | uint32 | Seconds | N/A | Read Only | Todays minimum battery voltage time UTC
64118 | 42 | 42 | 1 | R | FN_Todays_Maximum_Battery_Voltage | uint16 | Volts | FN_DC_Voltage_SF | Programmable | Todays maximum battery voltage
64118 | 43 | 44 | 2 | R | FN_Todays_Maximum_Battery_Time | uint32 | Seconds | N/A | Read Only | Todays maximum battery voltage time UTC
64118 | 45 | 45 | 1 | R | FN_Cycle_Charge_Factor | uint16 | Percent | N/A | Read Only | Cycle Charge Factor
64118 | 46 | 46 | 1 | R | FN_Cycle_kWh_Charge_Efficiency | uint16 | Percent | N/A | Read Only | Cycle kWh Charge Efficiency
64118 | 47 | 47 | 1 | R | FN_Total_Days_At_100_Percent | uint16 | Days | FN_Time_SF | Programmable | Total days at 100% charged
64118 | 48 | 48 | 1 | R | FN_Lifetime_kAH_Removed | uint16 | AH | N/A | Programmable | Lifetime kAH removed from battery
64118 | 49 | 49 | 1 | R | FN_Shunt_A_Historical_Returned_To_Battery_AH | uint16 | AH | N/A | Read Only | Shunt A historical returned to battery AH
64118 | 50 | 50 | 1 | R | FN_Shunt_A_Historical_Returned_To_Battery_kWh | uint16 | kWh | FN_kWh_SF | Read Only | Shunt A historical returned to battery kWh
64118 | 51 | 51 | 1 | R | FN_Shunt_A_Historical_Removed_From_Battery_AH | uint16 | AH | N/A | Read Only | Shunt A historical removed from battery AH
64118 | 52 | 52 | 1 | R | FN_Shunt_A_Historical_Removed_From_Battery_kWh | uint16 | kWh | FN_kWh_SF | Read Only | Shunt A historical removed from battery kWh
64118 | 53 | 53 | 1 | R | FN_Shunt_A_Maximum_Charge_Rate | uint16 | Amps | FN_DC_Current_SF | Read Only | Shunt A historical maximum charge rate Amps
64118 | 54 | 54 | 1 | R | FN_Shunt_A_Maximum_Charge_Rate_kW | uint16 | kW | FN_kWh_SF | Read Only | Shunt A historical maximum charge rate kW
64118 | 55 | 55 | 1 | R | FN_Shunt_A_Maximum_Discharge_Rate | int16 | Amps | FN_DC_Current_SF | Read Only | Shunt A historical maximum discharge rate Amps
64118 | 56 | 56 | 1 | R | FN_Shunt_A_Maximum_Discharge_Rate_kW | int16 | kW | FN_kWh_SF | Read Only | Shunt A historical maximum discharge rate kW
64118 | 57 | 57 | 1 | R | FN_Shunt_B_Historical_Returned_To_Battery_AH | uint16 | AH | N/A | Read Only | Shunt B historical returned to battery AH
64118 | 58 | 58 | 1 | R | FN_Shunt_B_Historical_Returned_To_Battery_kWh | uint16 | kWh | FN_kWh_SF | Read Only | Shunt B historical returned to battery kWh
64118 | 59 | 59 | 1 | R | FN_Shunt_B_Historical_Removed_From_Battery_AH | uint16 | AH | N/A | Read Only | Shunt B historical removed from battery AH
64118 | 60 | 60 | 1 | R | FN_Shunt_B_Historical_Removed_From_Battery_kWh | uint16 | kWh | FN_kWh_SF | Read Only | Shunt B historical removed from battery kWh
64118 | 61 | 61 | 1 | R | FN_Shunt_B_Maximum_Charge_Rate | uint16 | Amps | FN_DC_Current_SF | Read Only | Shunt B historical maximum charge rate Amps
64118 | 62 | 62 | 1 | R | FN_Shunt_B_Maximum_Charge_Rate_kW | uint16 | kW | FN_kWh_SF | Read Only | Shunt B historical maximum charge rate kW
64118 | 63 | 63 | 1 | R | FN_Shunt_B_Maximum_Discharge_Rate | int16 | Amps | FN_DC_Current_SF | Read Only | Shunt B historical maximum discharge rate Amps
64118 | 64 | 64 | 1 | R | FN_Shunt_B_Maximum_Discharge_Rate_kW | int16 | kW | FN_kWh_SF | Read Only | Shunt B historical maximum discharge rate kW
64118 | 65 | 65 | 1 | R | FN_Shunt_C_Historical_Returned_To_Battery_AH | uint16 | AH | N/A | Read Only | Shunt C historical returned to battery AH
64118 | 66 | 66 | 1 | R | FN_Shunt_C_Historical_Returned_To_Battery_kWh | uint16 | kWh | FN_kWh_SF | Read Only | Shunt C historical returned to battery kWh
64118 | 67 | 67 | 1 | R | FN_Shunt_C_Historical_Removed_From_Battery_AH | uint16 | AH | N/A | Read Only | Shunt C historical removed from battery AH
64118 | 68 | 68 | 1 | R | FN_Shunt_C_Historical_Removed_From_Battery_kWh | uint16 | kWh | FN_kWh_SF | Read Only | Shunt C historical removed from battery kWh
64118 | 69 | 69 | 1 | R | FN_Shunt_C_Maximum_Charge_Rate | uint16 | Amps | FN_DC_Current_SF | Read Only | Shunt C historical maximum charge rate Amps
64118 | 70 | 70 | 1 | R | FN_Shunt_C_Maximum_Charge_Rate_kW | uint16 | kW | FN_kWh_SF | Read Only | Shunt C historical maximum charge rate kW
64118 | 71 | 71 | 1 | R | FN_Shunt_C_Maximum_Discharge_Rate | int16 | Amps | FN_DC_Current_SF | Read Only | Shunt C historical maximum discharge rate Amps
64118 | 72 | 72 | 1 | R | FN_Shunt_C_Maximum_Discharge_Rate_kW | int16 | kW | FN_kWh_SF | Read Only | Shunt C historical maximum discharge rate kW
64118 | 73 | 73 | 1 | R | FN_Shunt_A_Reset_Maximum_Data | uint16 | N/A | N/A | Read Only | Read value needed to reset shunt A maximum data
64118 | 74 | 74 | 1 | W | FN_Shunt_A_Reset_Maximum_Data_Write_Complement | uint16 | N/A | N/A | Write Only | Write value's complement to reset shunt A maximum data
64118 | 75 | 75 | 1 | R | FN_Shunt_B_Reset_Maximum_Data | uint16 | N/A | N/A | Read Only | Read value needed to reset shunt B maximum data
64118 | 76 | 76 | 1 | W | FN_Shunt_B_Reset_Maximum_Data_Write_Complement | uint16 | N/A | N/A | Write Only | Write value's complement to reset shunt B maximum data
64118 | 77 | 77 | 1 | R | FN_Shunt_C_Reset_Maximum_Data | uint16 | N/A | N/A | Read Only | Read value needed to reset shunt C maximum data
64118 | 78 | 78 | 1 | W | FN_Shunt_C_Reset_Maximum_Data_Write_Complement | uint16 | N/A | N/A | Write Only | Write value's complement to reset shunt C maximum data
FN_Status Table
[9 empty] | Contents | Description
[9 empty] | 0x0001 | AUX relay enabled
[9 empty] | 0x0002 | Charge Parameters Met
Table 11 OutBack System Control Block
DID | Start | End | Size | R/W | Name | Type | Units | Scale Factor | Contents | Description
64120 | 1 | 1 | 1 | R | OB_DID | uint16 | N/A | N/A | 64120 | Vendor Extension for OutBack System Control Block
64120 | 2 | 2 | 1 | R | OB_Length | uint16 | Registers | N/A | 25 | Length of block in 16-bit registers
64120 | 3 | 3 | 1 | R | OB_DC_Voltage_SF | int16 | N/A | N/A | -1 | DC Voltage Scale Factor
64120 | 4 | 4 | 1 | R | OB_AC_Current_SF | int16 | N/A | N/A | -1 | AC Current Scale Factor
64120 | 5 | 5 | 1 | R | OB_Time_SF | int16 | N/A | N/A | -1 | Charge Time Scale Factor
64120 | 6 | 6 | 1 | W | OB_Bulk_Charge_Enable_Disable | uint16 | Enumerated | N/A | Programmable | 1=Start Bulk, 2=Stop Bulk, 3=Start EQ Charge, 4= Stop EQ Charge
64120 | 7 | 7 | 1 | W | OB_Inverter_AC_Drop_Use | uint16 | Enumerated | N/A | Programmable | 1=Use, 2=Drop
64120 | 8 | 8 | 1 | W | OB_Set_Inverter_Mode | uint16 | Enumerated | N/A | Programmable | 1=Off, 2=Search, 3=On
64120 | 9 | 9 | 1 | W | OB_Grid_Tie_Mode | uint16 | Enumerated | N/A | Programmable | 1=Enable, 2=Disable
64120 | 10 | 10 | 1 | W | OB_Set_Inverter_Charger_Mode | uint16 | Enumerated | N/A | Programmable | 1=Off, 2=Auto, 3=On
64120 | 11 | 11 | 1 | R | OB_Control_Status | uint16 | Bitfield | N/A | N/A | Bit field for status. See OB_Control_Status Table
64120 | 12 | 12 | 1 | R/W | OB_Set_Sell_Voltage | uint16 | Volts | OB_DC_Voltage_SF | Programmable | Global Sell Voltage
64120 | 13 | 13 | 1 | R/W | OB_Set_Radian_Inverter_Sell_Current_Limit | uint16 | Amps | OB_AC_Current_SF | Programmable | Radian Inverter Sell Current Limit
64120 | 14 | 14 | 1 | R/W | OB_Set_Absorb_Voltage | uint16 | Volts | OB_DC_Voltage_SF | Programmable | Global Absorb Voltage
64120 | 15 | 15 | 1 | R/W | OB_Set_Absorb_Time | uint16 | Hours | OB_Time_SF | Programmable | Time in tenths of hour
64120 | 16 | 16 | 1 | R/W | OB_Set_Float_Voltage | uint16 | Volts | OB_DC_Voltage_SF | Programmable | Global Float Voltage
64120 | 17 | 17 | 1 | R/W | OB_Set_Float_Time | uint16 | Hours | OB_Time_SF | Programmable | Time in tenths of hour
64120 | 18 | 18 | 1 | R/W | OB_Set_Inverter_Charger_Current_Limit | uint16 | Amps | OB_AC_Current_SF | Programmable | Inverter Charger Current Limit
64120 | 19 | 19 | 1 | R/W | OB_Set_Inverter_AC1_Current_Limit | uint16 | Amps | OB_AC_Current_SF | Programmable | Inverter AC1 input Current Limit
64120 | 20 | 20 | 1 | R/W | OB_Set_Inverter_AC2_Current_Limit | uint16 | Amps | OB_AC_Current_SF | Programmable | Inverter AC2 input Current Limit
64120 | 21 | 21 | 1 | R/W | OB_Set_AGS_OP_Mode | uint16 | Enumerated | N/A | Programmable | AGS Operating Mode: 0=Off, 1=On, 2=Auto
64120 | 22 | 22 | 1 | R | OB_AGS_Operational_State | uint16 | Enumerated | N/A | N/A | GEN_STOP=0, GEN_STARTING=1, GEN_RUNNING=2, GEN_WARMUP=3, GEN_COOLDOWN=4, GEN_AWAITING_AC=5
64120 | 23 | 23 | 1 | R | OB_AGS_Operational_State_Timer | uint16 | Seconds | N/A | Measured | Number of seconds that OB_AGS_Operational_State has been in current state. If Operational State is 0 then timer=0
64120 | 24 | 25 | 2 | R | OB_Gen_Last_Run_Start_Time_GMT | uint32 | Seconds | N/A | Measured | Generator last start time in GMT seconds
64120 | 26 | 27 | 2 | R | OB_Gen_Last_Start_Run_Duration | uint32 | Seconds | N/A | Measured | Last Generator Start Run Duration Seconds
OB_Control_Status Table
[9 empty] | Contents | Description
[9 empty] | 0x0001 | Absorb Charging
[9 empty] | 0x0002 | Float Charging
[9 empty] | 0x0004 | Inverter AC Input Use
[9 empty] | 0x0008 | Inverter Off
[9 empty] | 0x0010 | Inverter Search Mode
[9 empty] | 0x0020 | Inverter On
[9 empty] | 0x0040 | Inverter Grid-Tie Enabled
[9 empty] | 0x0080 | Inverter Charger Disabled
[9 empty] | 0x0100 | Inverter Charger Auto Mode
[9 empty] | 0x0200 | Inverter Charger Bulk and Float Mode
[9 empty] | 0x0400 | EQ Charging
[9 empty] | 0x0800 | Bulk Charging
[9 empty] | 0x1000 | SD Card Present
[9 empty] | 0x2000 | Replay File Present
[9 empty] | 0x4000 | SD Card Error
Table 12 SunSpec Common Model Block
DID | Start | End | Size | R/W | Field Name | Type | Units | Scale Factor | Contents | Description
1 | 1 | 1 | 1 | R | C_SunSpec_DID | uint16 | N/A | N/A | 1 | Uniquely identifies this as a SunSpec Common Model block
1 | 2 | 2 | 1 | R | C_SunSpec_Length | uint16 | Registers | N/A | 65 | Length of block in 16-bit registers
1 | 3 | 18 | 16 | R | C_Manufacturer | string (32) | N/A | N/A | Read Only
1 | 19 | 34 | 16 | R | C_Model | string (32) | N/A | N/A | Read Only
1 | 35 | 42 | 8 | R | C_Options | string (16) | N/A | N/A | Read Only
1 | 43 | 50 | 8 | R | C_Version | string (16) | N/A | N/A | Read Only
1 | 51 | 66 | 16 | R | C_SerialNumber | string (32) | N/A | N/A | Read Only
1 | 67 | 67 | 1 | R/W | C_DeviceAddress | uint16 | N/A | N/A | Write Only
Table 13 SunSpec Inverter - Single Phase
DID | Start | End | Size | R/W | Field Name | Type | Units | Scale Factor | Contents | Description
101 | 1 | 1 | 1 | R | C_SunSpec_DID | uint16 | N/A | N/A | 101 | Uniquely identifies this as a SunSpec Single Phase Inverter
101 | 2 | 2 | 1 | R | C_SunSpec_Length | uint16 | Registers | N/A | 50 | Length of model block
101 | 3 | 3 | 1 | R | I_AC_Current | uint16 | Amps | I_AC_Current_SF | Measured | AC Total Current value
101 | 4 | 4 | 1 | R | I_AC_CurrentA | uint16 | Amps | I_AC_Current_SF | Measured | AC Phase-A Current value
101 | 5 | 5 | 1 | R | I_AC_CurrentB | uint16 | Amps | I_AC_Current_SF | Measured | AC Phase-B Current value
101 | 6 | 6 | 1 | R | I_AC_CurrentC | uint16 | Amps | I_AC_Current_SF | Measured | AC Phase-C Current value
101 | 7 | 7 | 1 | R | I_AC_Current_SF | int16 | SF | N/A |  | AC Current Scale factor
101 | 8 | 8 | 1 | R | I_AC_VoltageAB | uint16 | Volts | I_AC_Voltage_SF | Measured | AC Voltage Phase-AB value
101 | 9 | 9 | 1 | R | I_AC_VoltageBC | uint16 | Volts | I_AC_Voltage_SF | Measured | AC Voltage Phase BC value
101 | 10 | 10 | 1 | R | I_AC_VoltageCA | uint16 | Volts | I_AC_Voltage_SF | Measured | AC Voltage Phase CA value
101 | 11 | 11 | 1 | R | I_AC_VoltageAN | uint16 | Volts | I_AC_Voltage_SF | Measured | AC Voltage Phase-A-to-neutral value
101 | 12 | 12 | 1 | R | I_AC_VoltageBN | uint16 | Volts | I_AC_Voltage_SF | Measured | AC Voltage Phase B-to-neutral value
101 | 13 | 13 | 1 | R | I_AC_VoltageCN | uint16 | Volts | I_AC_Voltage_SF | Measured | AC Voltage Phase C-to-neutral value
101 | 14 | 14 | 1 | R | I_AC_Voltage_SF | int16 | SF | N/A |  | AC Voltage Scale factor
101 | 15 | 15 | 1 | R | I_AC_Power | int16 | Watts | I_AC_Power_SF | Measured | AC Power value
101 | 16 | 16 | 1 | R | I_AC_Power_SF | int16 | SF | N/A |  | AC Power Scale factor
101 | 17 | 17 | 1 | R | I_AC_Frequency | uint16 | Hertz | I_AC_Frequency_SF | Measured | AC Frequency value
101 | 18 | 18 | 1 | R | I_AC_Frequency_SF | int16 | SF | N/A |  | Scale factor
101 | 19 | 19 | 1 | R | I_AC_VA | int16 | VA | I_AC_VA_SF | Measured | Apparent Power
101 | 20 | 20 | 1 | R | I_AC_VA_SF | int16 | SF | N/A |  | Scale factor
101 | 21 | 21 | 1 | R | I_AC_VAR | int16 | VAR | I_AC_VAR_SF | Measured | Reactive Power
101 | 22 | 22 | 1 | R | I_AC_VAR_SF | int16 | SF | N/A |  | Scale factor
101 | 23 | 23 | 1 | R | I_AC_PF | int16 | N/A | I_AC_PF_SF | Measured | Power Factor
101 | 24 | 24 | 1 | R | I_AC_PF_SF | int16 | SF | N/A |  | Scale factor
101 | 25 | 26 | 2 | R | I_AC_Energy_WH | uint32 | WattHours | I_AC_Energy_WH_SF | Measured | AC Lifetime Energy production
101 | 27 | 27 | 1 | R | I_AC_Energy_WH_SF | uint16 | SF | N/A | Measured | AC Lifetime Energy production scale factor
101 | 28 | 28 | 1 | R | I_DC_Current | uint16 | Amps | I_DC_Current_SF | Measured | DC Current value
101 | 29 | 29 | 1 | R | I_DC_Current_SF | int16 | SF | N/A |  | Scale factor
101 | 30 | 30 | 1 | R | I_DC_Voltage | uint16 | Volts | I_DC_Voltage_SF | Measured | DC Voltage value
101 | 31 | 31 | 1 | R | I_DC_Voltage_SF | int16 | SF | N/A |  | Scale factor
101 | 32 | 32 | 1 | R | I_DC_Power | int16 | Watts | I_DC_Power_SF | Measured | DC Power value
101 | 33 | 33 | 1 | R | I_DC_Power_SF | int16 | SF | N/A |  | Scale factor
101 | 34 | 34 | 1 | R | I_Temp_Cab | int16 | Degrees C | I_Temp_SF | Measured | Cabinet Temperature
101 | 35 | 35 | 1 | R | I_Temp_Sink | int16 | Degrees C | I_Temp_SF | Measured | Coolant or Heat Sink Temperature
101 | 36 | 36 | 1 | R | I_Temp_Trans | int16 | Degrees C | I_Temp_SF | Measured | Transformer Temperature
101 | 37 | 37 | 1 | R | I_Temp_Other | int16 | Degrees C | I_Temp_SF | Measured | Other Temperature
101 | 38 | 38 | 1 | R | I_Temp_SF | int16 | SF | N/A |  | Scale factor
101 | 39 | 39 | 1 | R | I_Status | uint16 | Enumerated | N/A | N/A | Operating State
101 | 40 | 40 | 1 | R | I_Status_Vendor | uint16 | Enumerated | N/A | N/A | Vendor Defined Operating State
101 | 41 | 42 | 2 | R | I_Event_1 | uint32 | Bitfield | N/A | N/A | Event Flags (bits 0-31)
101 | 43 | 44 | 2 | R | I_Event_2 | uint32 | Bitfield | N/A | N/A | Event Flags (bits 32-63) Future Use, set to 0
101 | 45 | 46 | 2 | R | I_Event_1_Vendor | uint32 | Bitfield | N/A | N/A | Vendor Defined Event Flags (bits 0-31)
101 | 47 | 48 | 2 | R | I_Event_2_Vendor | uint32 | Bitfield | N/A | N/A | Vendor Defined Event Flags (bits 32-63) Future Use
101 | 49 | 50 | 2 | R | I_Event_3_Vendor | uint32 | Bitfield | N/A | N/A | Vendor Defined Event Flags (bits 64-95) Future Use
101 | 51 | 52 | 2 | R | I_Event_4_Vendor | uint32 | Bitfield | N/A | N/A | Vendor Defined Event Flags (bits 96-127) Future Use
Table 14 SunSpec Inverter - Split Phase
DID | Start | End | Size | R/W | Field Name | Type | Units | Scale Factor | Contents | Description
102 | 1 | 1 | 1 | R | C_SunSpec_DID | uint16 | N/A | N/A | 102 | Uniquely identifies this as a SunSpec Split Phase Inverter
102 | 2 | 2 | 1 | R | C_SunSpec_Length | uint16 | Registers | N/A | 50 | Length of model block
102 | 3 | 3 | 1 | R | I_AC_Current | uint16 | Amps | I_AC_Current_SF | Measured | AC Total Current value
102 | 4 | 4 | 1 | R | I_AC_CurrentA | uint16 | Amps | I_AC_Current_SF | Measured | AC Phase-A Current value
102 | 5 | 5 | 1 | R | I_AC_CurrentB | uint16 | Amps | I_AC_Current_SF | Measured | AC Phase-B Current value
102 | 6 | 6 | 1 | R | I_AC_CurrentC | uint16 | Amps | I_AC_Current_SF | Measured | AC Phase-C Current value
102 | 7 | 7 | 1 | R | I_AC_Current_SF | int16 | SF | N/A |  | AC Current Scale factor
102 | 8 | 8 | 1 | R | I_AC_VoltageAB | uint16 | Volts | I_AC_Voltage_SF | Measured | AC Voltage Phase-AB value
102 | 9 | 9 | 1 | R | I_AC_VoltageBC | uint16 | Volts | I_AC_Voltage_SF | Measured | AC Voltage Phase BC value
102 | 10 | 10 | 1 | R | I_AC_VoltageCA | uint16 | Volts | I_AC_Voltage_SF | Measured | AC Voltage Phase CA value
102 | 11 | 11 | 1 | R | I_AC_VoltageAN | uint16 | Volts | I_AC_Voltage_SF | Measured | AC Voltage Phase-A-to-neutral value
102 | 12 | 12 | 1 | R | I_AC_VoltageBN | uint16 | Volts | I_AC_Voltage_SF | Measured | AC Voltage Phase B-to-neutral value
102 | 13 | 13 | 1 | R | I_AC_VoltageCN | uint16 | Volts | I_AC_Voltage_SF | Measured | AC Voltage Phase C-to-neutral value
102 | 14 | 14 | 1 | R | I_AC_Voltage_SF | int16 | SF | N/A |  | AC Voltage Scale factor
102 | 15 | 15 | 1 | R | I_AC_Power | int16 | Watts | I_AC_Power_SF | Measured | AC Power value
102 | 16 | 16 | 1 | R | I_AC_Power_SF | int16 | SF | N/A |  | AC Power Scale factor
102 | 17 | 17 | 1 | R | I_AC_Frequency | uint16 | Hertz | I_AC_Frequency_SF | Measured | AC Frequency value
102 | 18 | 18 | 1 | R | I_AC_Frequency_SF | int16 | SF | N/A |  | Scale factor
102 | 19 | 19 | 1 | R | I_AC_VA | int16 | VA | I_AC_VA_SF | Measured | Apparent Power
102 | 20 | 20 | 1 | R | I_AC_VA_SF | int16 | SF | N/A |  | Scale factor
102 | 21 | 21 | 1 | R | I_AC_VAR | int16 | VAR | I_AC_VAR_SF | Measured | Reactive Power
102 | 22 | 22 | 1 | R | I_AC_VAR_SF | int16 | SF | N/A |  | Scale factor
102 | 23 | 23 | 1 | R | I_AC_PF | int16 | N/A | I_AC_PF_SF | Measured | Power Factor
102 | 24 | 24 | 1 | R | I_AC_PF_SF | int16 | SF | N/A |  | Scale factor
102 | 25 | 26 | 2 | R | I_AC_Energy_WH | uint32 | WattHours | I_AC_Energy_WH_SF | Measured | AC Lifetime Energy production
102 | 27 | 27 | 1 | R | I_AC_Energy_WH_SF | uint16 | SF | N/A | Measured | AC Lifetime Energy production scale factor
102 | 28 | 28 | 1 | R | I_DC_Current | uint16 | Amps | I_DC_Current_SF | Measured | DC Current value
102 | 29 | 29 | 1 | R | I_DC_Current_SF | int16 | SF | N/A |  | Scale factor
102 | 30 | 30 | 1 | R | I_DC_Voltage | uint16 | Volts | I_DC_Voltage_SF | Measured | DC Voltage value
102 | 31 | 31 | 1 | R | I_DC_Voltage_SF | int16 | SF | N/A |  | Scale factor
102 | 32 | 32 | 1 | R | I_DC_Power | int16 | Watts | I_DC_Power_SF | Measured | DC Power value
102 | 33 | 33 | 1 | R | I_DC_Power_SF | int16 | SF | N/A |  | Scale factor
102 | 34 | 34 | 1 | R | I_Temp_Cab | int16 | Degrees C | I_Temp_SF | Measured | Cabinet Temperature
102 | 35 | 35 | 1 | R | I_Temp_Sink | int16 | Degrees C | I_Temp_SF | Measured | Coolant or Heat Sink Temperature
102 | 36 | 36 | 1 | R | I_Temp_Trans | int16 | Degrees C | I_Temp_SF | Measured | Transformer Temperature
102 | 37 | 37 | 1 | R | I_Temp_Other | int16 | Degrees C | I_Temp_SF | Measured | Other Temperature
102 | 38 | 38 | 1 | R | I_Temp_SF | int16 | SF | N/A |  | Scale factor
102 | 39 | 39 | 1 | R | I_Status | uint16 | Enumerated | N/A | N/A | Operating State
102 | 40 | 40 | 1 | R | I_Status_Vendor | uint16 | Enumerated | N/A | N/A | Vendor Defined Operating State
102 | 41 | 42 | 2 | R | I_Event_1 | uint32 | Bitfield | N/A | N/A | Event Flags (bits 0-31)
102 | 43 | 44 | 2 | R | I_Event_2 | uint32 | Bitfield | N/A | N/A | Event Flags (bits 32-63) Future Use, set to 0
102 | 45 | 46 | 2 | R | I_Event_1_Vendor | uint32 | Bitfield | N/A | N/A | Vendor Defined Event Flags (bits 0-31)
102 | 47 | 48 | 2 | R | I_Event_2_Vendor | uint32 | Bitfield | N/A | N/A | Vendor Defined Event Flags (bits 32-63) Future Use
102 | 49 | 50 | 2 | R | I_Event_3_Vendor | uint32 | Bitfield | N/A | N/A | Vendor Defined Event Flags (bits 64-95) Future Use
102 | 51 | 52 | 2 | R | I_Event_4_Vendor | uint32 | Bitfield | N/A | N/A | Vendor Defined Event Flags (bits 96-127) Future Use
Table 15 SunSpec Inverter - Three Phase
DID | Start | End | Size | R/W | Field Name | Type | Units | Scale Factor | Contents | Description
103 | 1 | 1 | 1 | R | C_SunSpec_DID | uint16 | N/A | N/A | 103 | Uniquely identifies this as a SunSpec Three Phase Inverter
103 | 2 | 2 | 1 | R | C_SunSpec_Length | uint16 | Registers | N/A | 50 | Length of model block
103 | 3 | 3 | 1 | R | I_AC_Current | uint16 | Amps | I_AC_Current_SF | Measured | AC Total Current value
103 | 4 | 4 | 1 | R | I_AC_CurrentA | uint16 | Amps | I_AC_Current_SF | Measured | AC Phase-A Current value
103 | 5 | 5 | 1 | R | I_AC_CurrentB | uint16 | Amps | I_AC_Current_SF | Measured | AC Phase-B Current value
103 | 6 | 6 | 1 | R | I_AC_CurrentC | uint16 | Amps | I_AC_Current_SF | Measured | AC Phase-C Current value
103 | 7 | 7 | 1 | R | I_AC_Current_SF | int16 | SF | N/A |  | AC Current Scale factor
103 | 8 | 8 | 1 | R | I_AC_VoltageAB | uint16 | Volts | I_AC_Voltage_SF | Measured | AC Voltage Phase-AB value
103 | 9 | 9 | 1 | R | I_AC_VoltageBC | uint16 | Volts | I_AC_Voltage_SF | Measured | AC Voltage Phase BC value
103 | 10 | 10 | 1 | R | I_AC_VoltageCA | uint16 | Volts | I_AC_Voltage_SF | Measured | AC Voltage Phase CA value
103 | 11 | 11 | 1 | R | I_AC_VoltageAN | uint16 | Volts | I_AC_Voltage_SF | Measured | AC Voltage Phase-A-to-neutral value
103 | 12 | 12 | 1 | R | I_AC_VoltageBN | uint16 | Volts | I_AC_Voltage_SF | Measured | AC Voltage Phase B-to-neutral value
103 | 13 | 13 | 1 | R | I_AC_VoltageCN | uint16 | Volts | I_AC_Voltage_SF | Measured | AC Voltage Phase C-to-neutral value
103 | 14 | 14 | 1 | R | I_AC_Voltage_SF | int16 | SF | N/A |  | AC Voltage Scale factor
103 | 15 | 15 | 1 | R | I_AC_Power | int16 | Watts | I_AC_Power_SF | Measured | AC Power value
103 | 16 | 16 | 1 | R | I_AC_Power_SF | int16 | SF | N/A |  | AC Power Scale factor
103 | 17 | 17 | 1 | R | I_AC_Frequency | uint16 | Hertz | I_AC_Frequency_SF | Measured | AC Frequency value
103 | 18 | 18 | 1 | R | I_AC_Frequency_SF | int16 | SF | N/A |  | Scale factor
103 | 19 | 19 | 1 | R | I_AC_VA | int16 | VA | I_AC_VA_SF | Measured | Apparent Power
103 | 20 | 20 | 1 | R | I_AC_VA_SF | int16 | SF | N/A |  | Scale factor
103 | 21 | 21 | 1 | R | I_AC_VAR | int16 | VAR | I_AC_VAR_SF | Measured | Reactive Power
103 | 22 | 22 | 1 | R | I_AC_VAR_SF | int16 | SF | N/A |  | Scale factor
103 | 23 | 23 | 1 | R | I_AC_PF | int16 | N/A | I_AC_PF_SF | Measured | Power Factor
103 | 24 | 24 | 1 | R | I_AC_PF_SF | int16 | SF | N/A |  | Scale factor
103 | 25 | 26 | 2 | R | I_AC_Energy_WH | uint32 | WattHours | I_AC_Energy_WH_SF | Measured | AC Lifetime Energy production
103 | 27 | 27 | 1 | R | I_AC_Energy_WH_SF | uint16 | SF | N/A | Measured | AC Lifetime Energy production scale factor
103 | 28 | 28 | 1 | R | I_DC_Current | uint16 | Amps | I_DC_Current_SF | Measured | DC Current value
103 | 29 | 29 | 1 | R | I_DC_Current_SF | int16 | SF | N/A |  | Scale factor
103 | 30 | 30 | 1 | R | I_DC_Voltage | uint16 | Volts | I_DC_Voltage_SF | Measured | DC Voltage value
103 | 31 | 31 | 1 | R | I_DC_Voltage_SF | int16 | SF | N/A |  | Scale factor
103 | 32 | 32 | 1 | R | I_DC_Power | int16 | Watts | I_DC_Power_SF | Measured | DC Power value
103 | 33 | 33 | 1 | R | I_DC_Power_SF | int16 | SF | N/A |  | Scale factor
103 | 34 | 34 | 1 | R | I_Temp_Cab | int16 | Degrees C | I_Temp_SF | Measured | Cabinet Temperature
103 | 35 | 35 | 1 | R | I_Temp_Sink | int16 | Degrees C | I_Temp_SF | Measured | Coolant or Heat Sink Temperature
103 | 36 | 36 | 1 | R | I_Temp_Trans | int16 | Degrees C | I_Temp_SF | Measured | Transformer Temperature
103 | 37 | 37 | 1 | R | I_Temp_Other | int16 | Degrees C | I_Temp_SF | Measured | Other Temperature
103 | 38 | 38 | 1 | R | I_Temp_SF | int16 | SF | N/A |  | Scale factor
103 | 39 | 39 | 1 | R | I_Status | uint16 | Enumerated | N/A | N/A | Operating State
103 | 40 | 40 | 1 | R | I_Status_Vendor | uint16 | Enumerated | N/A | N/A | Vendor Defined Operating State
103 | 41 | 42 | 2 | R | I_Event_1 | uint32 | Bitfield | N/A | N/A | Event Flags (bits 0-31)
103 | 43 | 44 | 2 | R | I_Event_2 | uint32 | Bitfield | N/A | N/A | Event Flags (bits 32-63) Future Use, set to 0
103 | 45 | 46 | 2 | R | I_Event_1_Vendor | uint32 | Bitfield | N/A | N/A | Vendor Defined Event Flags (bits 0-31)
103 | 47 | 48 | 2 | R | I_Event_2_Vendor | uint32 | Bitfield | N/A | N/A | Vendor Defined Event Flags (bits 32-63) Future Use
103 | 49 | 50 | 2 | R | I_Event_3_Vendor | uint32 | Bitfield | N/A | N/A | Vendor Defined Event Flags (bits 64-95) Future Use
103 | 51 | 52 | 2 | R | I_Event_4_Vendor | uint32 | Bitfield | N/A | N/A | Vendor Defined Event Flags (bits 96-127) Future Use
Table 16 OPTICS Packet Statistics
DID | Start | End | Size | R/W | Field Name | Type | Units | Scale Factor | Contents | Description
64255 | 1 | 1 | 1 | R | OP_stats_DID | uint16 | N/A | N/A | 64255 | OPTICS Packet Stats DID
64255 | 2 | 2 | 1 | R | OP_stats_Length | uint16 | Registers | N/A | 56 | Length of OPTICS Packet Status Block
64255 | 3 | 3 | 1 | R | OP_stats_Bt_min | uint16 | msecs | N/A | Measured | Boot packet minimum time
64255 | 4 | 4 | 1 | R | OP_stats_Bt_max | uint16 | msecs | N/A | Measured | Boot packet maximum time
64255 | 5 | 5 | 1 | R | OP_stats_Bt_ave | uint16 | msecs | N/A | Measured | Boot packet average time
64255 | 6 | 6 | 1 | R | OP_stats_Bt_attempts | uint16 | N/A | N/A | Measured | Boot packet number of attempts
64255 | 7 | 7 | 1 | R | OP_stats_Bt_errors | uint16 | N/A | N/A | Measured | Boot packet error returned from server count
64255 | 8 | 8 | 1 | R | OP_stats_Bt_timeouts | uint16 | N/A | N/A | Measured | Boot packet timeout from server count
64255 | 9 | 9 | 1 | R | OP_stats_Bt_packet_timeout | uint16 | secs | N/A | Measured | Boot packet current gateway timeout
64255 | 10 | 10 | 1 | R | OP_stats_Mp_min | uint16 | msecs | N/A | Measured | Map packet minimum time
64255 | 11 | 11 | 1 | R | OP_stats_Mp_max | uint16 | msecs | N/A | Measured | Map packet maximum time
64255 | 12 | 12 | 1 | R | OP_stats_Mp_ave | uint16 | msecs | N/A | Measured | Map packet average time
64255 | 13 | 13 | 1 | R | OP_stats_Mp_attempts | uint16 | N/A | N/A | Measured | Map packet number of attempts
64255 | 14 | 14 | 1 | R | OP_stats_Mp_errors | uint16 | N/A | N/A | Measured | Map packet error returned from server count
64255 | 15 | 15 | 1 | R | OP_stats_Mp_timeouts | uint16 | N/A | N/A | Measured | Map packet timeout from server count
64255 | 16 | 16 | 1 | R | OP_stats_Mp_packet_timeout | uint16 | secs | N/A | Measured | Map packet current gateway timeout
64255 | 17 | 17 | 1 | R | OP_stats_Cu_min | uint16 | msecs | N/A | Measured | Config packet minimum time
64255 | 18 | 18 | 1 | R | OP_stats_Cu_max | uint16 | msecs | N/A | Measured | Config packet maximum time
64255 | 19 | 19 | 1 | R | OP_stats_Cu_ave | uint16 | msecs | N/A | Measured | Config packet average time
64255 | 20 | 20 | 1 | R | OP_stats_Cu_attempts | uint16 | N/A | N/A | Measured | Config packet number of attempts
64255 | 21 | 21 | 1 | R | OP_stats_Cu_errors | uint16 | N/A | N/A | Measured | Config packet error returned from server count
64255 | 22 | 22 | 1 | R | OP_stats_Cu_timeouts | uint16 | N/A | N/A | Measured | Config packet timeout from server count
64255 | 23 | 23 | 1 | R | OP_stats_Cu_packet_timeout | uint16 | secs | N/A | Measured | Config packet current gateway timeout
64255 | 24 | 24 | 1 | R | OP_stats_Su_min | uint16 | msecs | N/A | Measured | Status packet minimum time
64255 | 25 | 25 | 1 | R | OP_stats_Su_max | uint16 | msecs | N/A | Measured | Status packet maximum time
64255 | 26 | 26 | 1 | R | OP_stats_Su_ave | uint16 | msecs | N/A | Measured | Status packet average time
64255 | 27 | 27 | 1 | R | OP_stats_Su_attempts | uint16 | N/A | N/A | Measured | Status packet number of attempts
64255 | 28 | 28 | 1 | R | OP_stats_Su_errors | uint16 | N/A | N/A | Measured | Status packet error returned from server count
64255 | 29 | 29 | 1 | R | OP_stats_Su_timeouts | uint16 | N/A | N/A | Measured | Status packet timeout from server count
64255 | 30 | 30 | 1 | R | OP_stats_Su_packet_timeout | uint16 | secs | N/A | Measured | Status packet current gateway timeout
64255 | 31 | 31 | 1 | R | OP_stats_Pg_min | uint16 | msecs | N/A | Measured | Ping packet minimum time
64255 | 32 | 32 | 1 | R | OP_stats_Pg_max | uint16 | msecs | N/A | Measured | Ping packet maximum time
64255 | 33 | 33 | 1 | R | OP_stats_Pg_ave | uint16 | msecs | N/A | Measured | Ping packet average time
64255 | 34 | 34 | 1 | R | OP_stats_Pg_attempts | uint16 | N/A | N/A | Measured | Ping packet number of attempts
64255 | 35 | 35 | 1 | R | OP_stats_Pg_errors | uint16 | N/A | N/A | Measured | Ping packet error returned from server count
64255 | 36 | 36 | 1 | R | OP_stats_Pg_timeouts | uint16 | N/A | N/A | Measured | Ping packet timeout from server count
64255 | 37 | 37 | 1 | R | OP_stats_Pg_packet_timeout | uint16 | secs | N/A | Measured | Ping packet current gateway timeout
64255 | 38 | 38 | 1 | R | OP_stats_Mb_min | uint16 | msecs | N/A | Measured | Modbus packet minimum time
64255 | 39 | 39 | 1 | R | OP_stats_Mb_max | uint16 | msecs | N/A | Measured | Modbus packet maximum time
64255 | 40 | 40 | 1 | R | OP_stats_Mb_ave | uint16 | msecs | N/A | Measured | Modbus packet average time
64255 | 41 | 41 | 1 | R | OP_stats_Mb_attempts | uint16 | N/A | N/A | Measured | Modbus packet number of attempts
64255 | 42 | 42 | 1 | R | OP_stats_Mb_errors | uint16 | N/A | N/A | Measured | Modbus packet error returned from server count
64255 | 43 | 43 | 1 | R | OP_stats_Mb_timeouts | uint16 | N/A | N/A | Measured | Modbus packet timeout from server count
64255 | 44 | 44 | 1 | R | OP_stats_Mb_packet_timeout | uint16 | secs | N/A | Measured | Modbus packet current gateway timeout
64255 | 45 | 45 | 1 | R | OP_stats_Fu_min | uint16 | msecs | N/A | Measured | File IO packet minimum time
64255 | 46 | 46 | 1 | R | OP_stats_Fu_max | uint16 | msecs | N/A | Measured | File IO packet maximum time
64255 | 47 | 47 | 1 | R | OP_stats_Fu_ave | uint16 | msecs | N/A | Measured | File IO packet average time
64255 | 48 | 48 | 1 | R | OP_stats_Fu_attempts | uint16 | N/A | N/A | Measured | File IO packet number of attempts
64255 | 49 | 49 | 1 | R | OP_stats_Fu_errors | uint16 | N/A | N/A | Measured | File IO packet error returned from server count
64255 | 50 | 50 | 1 | R | OP_stats_Fu_timeouts | uint16 | N/A | N/A | Measured | File IO packet timeout from server count
64255 | 51 | 51 | 1 | R | OP_stats_Fu_packet_timeout | uint16 | secs | N/A | Measured | File IO packet current gateway timeout
64255 | 52 | 52 | 1 | R | OP_stats_Ev_min | uint16 | msecs | N/A | Measured | Event packet minimum time
64255 | 53 | 53 | 1 | R | OP_stats_Ev_max | uint16 | msecs | N/A | Measured | Event packet maximum time
64255 | 54 | 54 | 1 | R | OP_stats_Ev_ave | uint16 | msecs | N/A | Measured | Event packet average time
64255 | 55 | 55 | 1 | R | OP_stats_Ev_attempts | uint16 | N/A | N/A | Measured | Event packet number of attempts
64255 | 56 | 56 | 1 | R | OP_stats_Ev_errors | uint16 | N/A | N/A | Measured | Event packet error returned from server count
64255 | 57 | 57 | 1 | R | OP_stats_Ev_timeouts | uint16 | N/A | N/A | Measured | Event packet timeout from server count
64255 | 58 | 58 | 1 | R | OP_stats_Ev_packet_timeout | uint16 | secs | N/A | Measured | Event packet current gateway timeout
Table 16 UPS Inverters
DID | Start | End | Size | R/W | Field Name | Type | Units | Scale Factor | Contents | Description
1001 | 0 | 0 | 1 | R | Relay_1_(K1) | INTEGER | N/A | N/A |  | Relay 1 (K1)
1002 | 0 | 0 | 1 | R | Relay_2_(K2) | INTEGER | N/A | N/A |  | Relay 2 (K2)
1003 | 0 | 0 | 1 | R | Relay_3_(K3) | INTEGER | N/A | N/A |  | Relay 3 (K3)
1004 | 0 | 0 | 1 | R | Relay_4_(K4) | INTEGER | N/A | N/A |  | Relay 4 (K4)
1005 | 0 | 0 | 1 | R | Relay_5_(K5) | INTEGER | N/A | N/A |  | Relay 5 (K5)
1006 | 0 | 0 | 1 | R | Relay_6_(K6) | INTEGER | N/A | N/A |  | Relay 6 (K6)
1007 | 0 | 0 | 1 | R | Relay_7_(K7) | INTEGER | N/A | N/A |  | Relay 7 (K7)
1008 | 0 | 0 | 1 | R | Relay_8_(K8) | INTEGER | N/A | N/A |  | Relay 8 (K8)
1009 | 0 | 0 | 1 | R | Relay_9_(K9) | INTEGER | N/A | N/A |  | Relay 9 (K9)
1010 | 0 | 0 | 1 | R | Relay_10_(K10) | INTEGER | N/A | N/A |  | Relay 10 (K10)
1011 | 0 | 0 | 1 | R | Relay_11_(K11) | INTEGER | N/A | N/A |  | Relay 11 (K11)
1012 | 0 | 0 | 1 | R | Relay_12_(K12) | INTEGER | N/A | N/A |  | Relay 12 (K12)
1013 | 0 | 0 | 1 | R | Relay_13_(K13) | INTEGER | N/A | N/A |  | Relay 13 (K13)
1014 | 0 | 0 | 1 | R | Relay_14_(K14) | INTEGER | N/A | N/A |  | Relay 14 (K14)
1015 | 0 | 0 | 1 | R | Relay_15_(K15) | INTEGER | N/A | N/A |  | Relay 15 (K15)
1016 | 0 | 0 | 1 | R | Relay_16_(K16) | INTEGER | N/A | N/A |  | Relay 16 (K16)
1017 | 0 | 0 | 1 | R | Rectifier_Fail | INTEGER | N/A | N/A |  | Rectifier Fail
1018 | 0 | 0 | 1 | R | Rectifier_Minor | INTEGER | N/A | N/A |  | Rectifier Minor
1019 | 0 | 0 | 1 | R | Rect._Major_Fail_Count | INTEGER | N/A | N/A |  | Rect. Major Fail Count
1020 | 0 | 0 | 1 | R | Rect._Minor_Fail_Count | INTEGER | N/A | N/A |  | Rect. Minor Fail Count
1021 | 0 | 0 | 1 | R | Rectifier_Lockout | INTEGER | N/A | N/A |  | Rectifier Lockout
1022 | 0 | 0 | 1 | R | Out_Of_Tolerance | INTEGER | N/A | N/A |  | Out Of Tolerance
1023 | 0 | 0 | 1 | R | Rect._Comms_Lost | INTEGER | N/A | N/A |  | Rect. Comms Lost
1024 | 0 | 0 | 1 | R | Rect._Equalize_Activated | INTEGER | N/A | N/A |  | Rect. Equalize Activated
1025 | 0 | 0 | 1 | R | Rect._AC_Mains_Fail | INTEGER | N/A | N/A |  | Rect. AC Mains Fail
1026 | 0 | 0 | 1 | R | Max_Rectifiers_Exceeded | INTEGER | N/A | N/A |  | Max Rectifiers Exceeded
1027 | 0 | 0 | 1 | R | Fan_Fail_Alarm | INTEGER | N/A | N/A |  | Fan Fail Alarm
1028 | 0 | 0 | 1 | R | Power_Save | INTEGER | N/A | N/A |  | Power Save
1029 | 0 | 0 | 1 | R | Urgent_Rect._AC_Mains_Fail | INTEGER | N/A | N/A |  | Urgent Rect. AC Mains Fail
1030 | 0 | 0 | 1 | R | Bypass_Mode_On | INTEGER | N/A | N/A |  | Bypass Mode On
1031 | 0 | 0 | 1 | R | Inverter_Output_Breaker_Off | INTEGER | N/A | N/A |  | Inverter Output Breaker Off
1032 | 0 | 0 | 1 | R | TVSS | INTEGER | N/A | N/A |  | TVSS
1033 | 0 | 0 | 1 | R | Inverter_Input_Breaker_Off | INTEGER | N/A | N/A |  | Inverter Input Breaker Off
1034 | 0 | 0 | 1 | R | D5_FXR_AC/DC_Input_CB | INTEGER | N/A | N/A |  | D5 FXR AC/DC Input CB
1035 | 0 | 0 | 1 | R | D6_PV_Charger_CB | INTEGER | N/A | N/A |  | D6 PV Charger CB
1036 | 0 | 0 | 1 | R | D7_PV_Rack_Main_CB | INTEGER | N/A | N/A |  | D7 PV Rack Main CB
1037 | 0 | 0 | 1 | R | D8_PV_Rack_Batt_CB | INTEGER | N/A | N/A |  | D8 PV Rack Batt CB
1038 | 0 | 0 | 1 | R | Battery_Current_High | INTEGER | N/A | N/A |  | Battery Current High
1039 | 0 | 0 | 1 | R | Load_Current_High | INTEGER | N/A | N/A |  | Load Current High
1040 | 0 | 0 | 1 | R | AC_Mains_High | INTEGER | N/A | N/A |  | AC Mains High
1041 | 0 | 0 | 1 | R | AC_Mains_Low | INTEGER | N/A | N/A |  | AC Mains Low
1042 | 0 | 0 | 1 | R | High_Voltage_1 | INTEGER | N/A | N/A |  | High Voltage 1
1043 | 0 | 0 | 1 | R | High_Voltage_2 | INTEGER | N/A | N/A |  | High Voltage 2
1044 | 0 | 0 | 1 | R | Low_Voltage_1 | INTEGER | N/A | N/A |  | Low Voltage 1
1045 | 0 | 0 | 1 | R | Low_Voltage_2 | INTEGER | N/A | N/A |  | Low Voltage 2
1046 | 0 | 0 | 1 | R | Midpoint_Monitor_1 | INTEGER | N/A | N/A |  | Midpoint Monitor 1
1047 | 0 | 0 | 1 | R | Midpoint_Monitor_2 | INTEGER | N/A | N/A |  | Midpoint Monitor 2
1048 | 0 | 0 | 1 | R | Midpoint_Monitor_3 | INTEGER | N/A | N/A |  | Midpoint Monitor 3
1049 | 0 | 0 | 1 | R | Midpoint_Monitor_4 | INTEGER | N/A | N/A |  | Midpoint Monitor 4
1050 | 0 | 0 | 1 | R | Midpoint_Monitor_5 | INTEGER | N/A | N/A |  | Midpoint Monitor 5
1051 | 0 | 0 | 1 | R | Battery_Runtime_Low | INTEGER | N/A | N/A |  | Battery Runtime Low
1052 | 0 | 0 | 1 | R | Battery_Capacity_Low | INTEGER | N/A | N/A |  | Battery Capacity Low
1053 | 0 | 0 | 1 | R | Battery_Overtemp | INTEGER | N/A | N/A |  | Battery Overtemp
1054 | 0 | 0 | 1 | R | Battery_On_Discharge | INTEGER | N/A | N/A |  | Battery On Discharge
1055 | 0 | 0 | 1 | R | Battery_Test_Alarm | INTEGER | N/A | N/A |  | Battery Test Alarm
1056 | 0 | 0 | 1 | R | Boost_Mode_Alarm | INTEGER | N/A | N/A |  | Boost Mode Alarm
1057 | 0 | 0 | 1 | R | Temp_Sensor_1_Fail | INTEGER | N/A | N/A |  | Temp Sensor 1 Fail
1058 | 0 | 0 | 1 | R | Temp_Sensor_2_Fail | INTEGER | N/A | N/A |  | Temp Sensor 2 Fail
1059 | 0 | 0 | 1 | R | Temp_Sensor_3_Fail | INTEGER | N/A | N/A |  | Temp Sensor 3 Fail
1060 | 0 | 0 | 1 | R | Temp_Sensor_4_Fail | INTEGER | N/A | N/A |  | Temp Sensor 4 Fail
1061 | 0 | 0 | 1 | R | TC_Sensor_Fail | INTEGER | N/A | N/A |  | TC Sensor Fail
1062 | 0 | 0 | 1 | R | Peak_Billing | INTEGER | N/A | N/A |  | Peak Billing
1063 | 0 | 0 | 1 | R | Custom_2 | INTEGER | N/A | N/A |  | Custom 2
1064 | 0 | 0 | 1 | R | Custom_3 | INTEGER | N/A | N/A |  | Custom 3
1065 | 0 | 0 | 1 | R | Custom_4 | INTEGER | N/A | N/A |  | Custom 4
1066 | 0 | 0 | 1 | R | Custom_5 | INTEGER | N/A | N/A |  | Custom 5
1067 | 0 | 0 | 1 | R | Custom_6 | INTEGER | N/A | N/A |  | Custom 6
1068 | 0 | 0 | 1 | R | Custom_7 | INTEGER | N/A | N/A |  | Custom 7
1069 | 0 | 0 | 1 | R | Custom_8 | INTEGER | N/A | N/A |  | Custom 8
1070 | 0 | 0 | 1 | R | Custom_9 | INTEGER | N/A | N/A |  | Custom 9
1071 | 0 | 0 | 1 | R | Low_AC_Output_Power | INTEGER | N/A | N/A |  | Low AC Output Power
1072 | 0 | 0 | 1 | R | DC_Mode | INTEGER | N/A | N/A |  | DC Mode
1073 | 0 | 0 | 1 | R | Custom_12 | INTEGER | N/A | N/A |  | Custom 12
1074 | 0 | 0 | 1 | R | Custom_13 | INTEGER | N/A | N/A |  | Custom 13
1075 | 0 | 0 | 1 | R | Custom_14 | INTEGER | N/A | N/A |  | Custom 14
1076 | 0 | 0 | 1 | R | Custom_15 | INTEGER | N/A | N/A |  | Custom 15
1077 | 0 | 0 | 1 | R | Custom_16 | INTEGER | N/A | N/A |  | Custom 16
1078 | 0 | 0 | 1 | R | Custom_17 | INTEGER | N/A | N/A |  | Custom 17
1079 | 0 | 0 | 1 | R | Custom_18 | INTEGER | N/A | N/A |  | Custom 18
1080 | 0 | 0 | 1 | R | Custom_19 | INTEGER | N/A | N/A |  | Custom 19
1081 | 0 | 0 | 1 | R | Custom_20 | INTEGER | N/A | N/A |  | Custom 20
1082 | 0 | 0 | 1 | R | Real_Time_Clock_Error | INTEGER | N/A | N/A |  | Real Time Clock Error
1083 | 0 | 0 | 1 | R | Invalid_Device_Firmware | INTEGER | N/A | N/A |  | Invalid Device Firmware
1084 | 0 | 0 | 1 | R | Ground_Fault_Detected | INTEGER | N/A | N/A |  | Ground Fault Detected
1085 | 0 | 0 | 1 | R | Improper_Controller_Shutdown | INTEGER | N/A | N/A |  | Improper Controller Shutdown
1086 | 0 | 0 | 1 | R | Invalid_Battery_Voltage | INTEGER | N/A | N/A |  | Invalid Battery Voltage
1087 | 0 | 0 | 1 | R | System_Major | INTEGER | N/A | N/A |  | System Major
1088 | 0 | 0 | 1 | R | System_Minor | INTEGER | N/A | N/A |  | System Minor
1089 | 0 | 0 | 1 | R | LVD_1 | INTEGER | N/A | N/A |  | LVD 1
1090 | 0 | 0 | 1 | R | LVD_2 | INTEGER | N/A | N/A |  | LVD 2
1091 | 0 | 0 | 1 | R | LVD_3 | INTEGER | N/A | N/A |  | LVD 3
1092 | 0 | 0 | 1 | R | LVD_4 | INTEGER | N/A | N/A |  | LVD 4
1093 | 0 | 0 | 1 | R | LVD_5 | INTEGER | N/A | N/A |  | LVD 5
1094 | 0 | 0 | 1 | R | LVD_6 | INTEGER | N/A | N/A |  | LVD 6
1095 | 0 | 0 | 1 | R | LVD_7 | INTEGER | N/A | N/A |  | LVD 7
1096 | 0 | 0 | 1 | R | LVD_8 | INTEGER | N/A | N/A |  | LVD 8
1097 | 0 | 0 | 1 | R | LVD_9 | INTEGER | N/A | N/A |  | LVD 9
1098 | 0 | 0 | 1 | R | LVD_10 | INTEGER | N/A | N/A |  | LVD 10
1099 | 0 | 0 | 1 | R | CEMF_Control | INTEGER | N/A | N/A |  | CEMF Control
1100 | 0 | 0 | 1 | R | HVSD_Control | INTEGER | N/A | N/A |  | HVSD Control
1101 | 0 | 0 | 1 | R | LVD_Inhibit | INTEGER | N/A | N/A |  | LVD Inhibit
1102 | 0 | 0 | 1 | R | Cell_Deviation_1 | INTEGER | N/A | N/A |  | Cell Deviation 1
1103 | 0 | 0 | 1 | R | Current_Alarm_1 | INTEGER | N/A | N/A |  | Current Alarm 1
1104 | 0 | 0 | 1 | R | Voltage_Alarm_1 | INTEGER | N/A | N/A |  | Voltage Alarm 1
1105 | 0 | 0 | 1 | R | Temperature_Alarm_1 | INTEGER | N/A | N/A |  | Temperature Alarm 1
1106 | 0 | 0 | 1 | R | Comms_Alarm_1 | INTEGER | N/A | N/A |  | Comms Alarm 1
1107 | 0 | 0 | 1 | R | Cell_Deviation_2 | INTEGER | N/A | N/A |  | Cell Deviation 2
1108 | 0 | 0 | 1 | R | Current_Alarm_2 | INTEGER | N/A | N/A |  | Current Alarm 2
1109 | 0 | 0 | 1 | R | Voltage_Alarm_2 | INTEGER | N/A | N/A |  | Voltage Alarm 2
1110 | 0 | 0 | 1 | R | Temperature_Alarm_2 | INTEGER | N/A | N/A |  | Temperature Alarm 2
1111 | 0 | 0 | 1 | R | Comms_Alarm_2 | INTEGER | N/A | N/A |  | Comms Alarm 2
1112 | 0 | 0 | 1 | R | Cell_Deviation_3 | INTEGER | N/A | N/A |  | Cell Deviation 3
1113 | 0 | 0 | 1 | R | Current_Alarm_3 | INTEGER | N/A | N/A |  | Current Alarm 3
1114 | 0 | 0 | 1 | R | Voltage_Alarm_3 | INTEGER | N/A | N/A |  | Voltage Alarm 3
1115 | 0 | 0 | 1 | R | Temperature_Alarm_3 | INTEGER | N/A | N/A |  | Temperature Alarm 3
1116 | 0 | 0 | 1 | R | Comms_Alarm_3 | INTEGER | N/A | N/A |  | Comms Alarm 3
1117 | 0 | 0 | 1 | R | Cell_Deviation_4 | INTEGER | N/A | N/A |  | Cell Deviation 4
1118 | 0 | 0 | 1 | R | Current_Alarm_4 | INTEGER | N/A | N/A |  | Current Alarm 4
1119 | 0 | 0 | 1 | R | Voltage_Alarm_4 | INTEGER | N/A | N/A |  | Voltage Alarm 4
1120 | 0 | 0 | 1 | R | Temperature_Alarm_4 | INTEGER | N/A | N/A |  | Temperature Alarm 4
1121 | 0 | 0 | 1 | R | Comms_Alarm_4 | INTEGER | N/A | N/A |  | Comms Alarm 4
1122 | 0 | 0 | 1 | R | Cell_Deviation_5 | INTEGER | N/A | N/A |  | Cell Deviation 5
1123 | 0 | 0 | 1 | R | Current_Alarm_5 | INTEGER | N/A | N/A |  | Current Alarm 5
1124 | 0 | 0 | 1 | R | Voltage_Alarm_5 | INTEGER | N/A | N/A |  | Voltage Alarm 5
1125 | 0 | 0 | 1 | R | Temperature_Alarm_5 | INTEGER | N/A | N/A |  | Temperature Alarm 5
1126 | 0 | 0 | 1 | R | Comms_Alarm_5 | INTEGER | N/A | N/A |  | Comms Alarm 5
1127 | 0 | 0 | 1 | R | Cell_Deviation_6 | INTEGER | N/A | N/A |  | Cell Deviation 6
1128 | 0 | 0 | 1 | R | Current_Alarm_6 | INTEGER | N/A | N/A |  | Current Alarm 6
1129 | 0 | 0 | 1 | R | Voltage_Alarm_6 | INTEGER | N/A | N/A |  | Voltage Alarm 6
1130 | 0 | 0 | 1 | R | Temperature_Alarm_6 | INTEGER | N/A | N/A |  | Temperature Alarm 6
1131 | 0 | 0 | 1 | R | Comms_Alarm_6 | INTEGER | N/A | N/A |  | Comms Alarm 6
1132 | 0 | 0 | 1 | R | Cell_Deviation_7 | INTEGER | N/A | N/A |  | Cell Deviation 7
1133 | 0 | 0 | 1 | R | Current_Alarm_7 | INTEGER | N/A | N/A |  | Current Alarm 7
1134 | 0 | 0 | 1 | R | Voltage_Alarm_7 | INTEGER | N/A | N/A |  | Voltage Alarm 7
1135 | 0 | 0 | 1 | R | Temperature_Alarm_7 | INTEGER | N/A | N/A |  | Temperature Alarm 7
1136 | 0 | 0 | 1 | R | Comms_Alarm_7 | INTEGER | N/A | N/A |  | Comms Alarm 7
1137 | 0 | 0 | 1 | R | Cell_Deviation_8 | INTEGER | N/A | N/A |  | Cell Deviation 8
1138 | 0 | 0 | 1 | R | Current_Alarm_8 | INTEGER | N/A | N/A |  | Current Alarm 8
1139 | 0 | 0 | 1 | R | Voltage_Alarm_8 | INTEGER | N/A | N/A |  | Voltage Alarm 8
1140 | 0 | 0 | 1 | R | Temperature_Alarm_8 | INTEGER | N/A | N/A |  | Temperature Alarm 8
1141 | 0 | 0 | 1 | R | Comms_Alarm_8 | INTEGER | N/A | N/A |  | Comms Alarm 8
1142 | 0 | 0 | 1 | R | Cell_Deviation_9 | INTEGER | N/A | N/A |  | Cell Deviation 9
1143 | 0 | 0 | 1 | R | Current_Alarm_9 | INTEGER | N/A | N/A |  | Current Alarm 9
1144 | 0 | 0 | 1 | R | Voltage_Alarm_9 | INTEGER | N/A | N/A |  | Voltage Alarm 9
1145 | 0 | 0 | 1 | R | Temperature_Alarm_9 | INTEGER | N/A | N/A |  | Temperature Alarm 9
1146 | 0 | 0 | 1 | R | Comms_Alarm_9 | INTEGER | N/A | N/A |  | Comms Alarm 9
1147 | 0 | 0 | 1 | R | Cell_Deviation_10 | INTEGER | N/A | N/A |  | Cell Deviation 10
1148 | 0 | 0 | 1 | R | Current_Alarm_10 | INTEGER | N/A | N/A |  | Current Alarm 10
1149 | 0 | 0 | 1 | R | Voltage_Alarm_10 | INTEGER | N/A | N/A |  | Voltage Alarm 10
1150 | 0 | 0 | 1 | R | Temperature_Alarm_10 | INTEGER | N/A | N/A |  | Temperature Alarm 10
1151 | 0 | 0 | 1 | R | Comms_Alarm_10 | INTEGER | N/A | N/A |  | Comms Alarm 10
1152 | 0 | 0 | 1 | R | Cell_Deviation_11 | INTEGER | N/A | N/A |  | Cell Deviation 11
1153 | 0 | 0 | 1 | R | Current_Alarm_11 | INTEGER | N/A | N/A |  | Current Alarm 11
1154 | 0 | 0 | 1 | R | Voltage_Alarm_11 | INTEGER | N/A | N/A |  | Voltage Alarm 11
1155 | 0 | 0 | 1 | R | Temperature_Alarm_11 | INTEGER | N/A | N/A |  | Temperature Alarm 11
1156 | 0 | 0 | 1 | R | Comms_Alarm_11 | INTEGER | N/A | N/A |  | Comms Alarm 11
1157 | 0 | 0 | 1 | R | Cell_Deviation_12 | INTEGER | N/A | N/A |  | Cell Deviation 12
1158 | 0 | 0 | 1 | R | Current_Alarm_12 | INTEGER | N/A | N/A |  | Current Alarm 12
1159 | 0 | 0 | 1 | R | Voltage_Alarm_12 | INTEGER | N/A | N/A |  | Voltage Alarm 12
1160 | 0 | 0 | 1 | R | Temperature_Alarm_12 | INTEGER | N/A | N/A |  | Temperature Alarm 12
1161 | 0 | 0 | 1 | R | Comms_Alarm_12 | INTEGER | N/A | N/A |  | Comms Alarm 12
1162 | 0 | 0 | 1 | R | Cell_Deviation_13 | INTEGER | N/A | N/A |  | Cell Deviation 13
1163 | 0 | 0 | 1 | R | Current_Alarm_13 | INTEGER | N/A | N/A |  | Current Alarm 13
1164 | 0 | 0 | 1 | R | Voltage_Alarm_13 | INTEGER | N/A | N/A |  | Voltage Alarm 13
1165 | 0 | 0 | 1 | R | Temperature_Alarm_13 | INTEGER | N/A | N/A |  | Temperature Alarm 13
1166 | 0 | 0 | 1 | R | Comms_Alarm_13 | INTEGER | N/A | N/A |  | Comms Alarm 13
1167 | 0 | 0 | 1 | R | Cell_Deviation_14 | INTEGER | N/A | N/A |  | Cell Deviation 14
1168 | 0 | 0 | 1 | R | Current_Alarm_14 | INTEGER | N/A | N/A |  | Current Alarm 14
1169 | 0 | 0 | 1 | R | Voltage_Alarm_14 | INTEGER | N/A | N/A |  | Voltage Alarm 14
1170 | 0 | 0 | 1 | R | Temperature_Alarm_14 | INTEGER | N/A | N/A |  | Temperature Alarm 14
1171 | 0 | 0 | 1 | R | Comms_Alarm_14 | INTEGER | N/A | N/A |  | Comms Alarm 14
1172 | 0 | 0 | 1 | R | Cell_Deviation_15 | INTEGER | N/A | N/A |  | Cell Deviation 15
1173 | 0 | 0 | 1 | R | Current_Alarm_15 | INTEGER | N/A | N/A |  | Current Alarm 15
1174 | 0 | 0 | 1 | R | Voltage_Alarm_15 | INTEGER | N/A | N/A |  | Voltage Alarm 15
1175 | 0 | 0 | 1 | R | Temperature_Alarm_15 | INTEGER | N/A | N/A |  | Temperature Alarm 15
1176 | 0 | 0 | 1 | R | Comms_Alarm_15 | INTEGER | N/A | N/A |  | Comms Alarm 15
1177 | 0 | 0 | 1 | R | Cell_Deviation_16 | INTEGER | N/A | N/A |  | Cell Deviation 16
1178 | 0 | 0 | 1 | R | Current_Alarm_16 | INTEGER | N/A | N/A |  | Current Alarm 16
1179 | 0 | 0 | 1 | R | Voltage_Alarm_16 | INTEGER | N/A | N/A |  | Voltage Alarm 16
1180 | 0 | 0 | 1 | R | Temperature_Alarm_16 | INTEGER | N/A | N/A |  | Temperature Alarm 16
1181 | 0 | 0 | 1 | R | Comms_Alarm_16 | INTEGER | N/A | N/A |  | Comms Alarm 16
1182 | 0 | 0 | 1 | R | Converter_Fail | INTEGER | N/A | N/A |  | Converter Fail
1183 | 0 | 0 | 1 | R | Converter_Minor | INTEGER | N/A | N/A |  | Converter Minor
1184 | 0 | 0 | 1 | R | Conv._Major_Fail_Count | INTEGER | N/A | N/A |  | Conv. Major Fail Count
1185 | 0 | 0 | 1 | R | Conv._Minor_Fail_Count | INTEGER | N/A | N/A |  | Conv. Minor Fail Count
1186 | 0 | 0 | 1 | R | Conv._Out_Of_Tolerance | INTEGER | N/A | N/A |  | Conv. Out Of Tolerance
1187 | 0 | 0 | 1 | R | Conv._Comms_Lost | INTEGER | N/A | N/A |  | Conv. Comms Lost
1188 | 0 | 0 | 1 | R | Conv._Input_Voltage_Fail | INTEGER | N/A | N/A |  | Conv. Input Voltage Fail
1189 | 0 | 0 | 1 | R | Conv._Fan_Fail | INTEGER | N/A | N/A |  | Conv. Fan Fail
1190 | 0 | 0 | 1 | R | Conv._Load_Current_High | INTEGER | N/A | N/A |  | Conv. Load Current High
1191 | 0 | 0 | 1 | R | Conv._Low_Output_Voltage | INTEGER | N/A | N/A |  | Conv. Low Output Voltage
1192 | 0 | 0 | 1 | R | Conv._High_Output_Voltage | INTEGER | N/A | N/A |  | Conv. High Output Voltage
1193 | 0 | 0 | 1 | R | Inverter_Major_Fail_Count | INTEGER | N/A | N/A |  | Inverter Major Fail Count
1194 | 0 | 0 | 1 | R | Inverter_Minor_Fail_Count | INTEGER | N/A | N/A |  | Inverter Minor Fail Count
1195 | 0 | 0 | 1 | R | Inverter_Comms_Lost | INTEGER | N/A | N/A |  | Inverter Comms Lost
1196 | 0 | 0 | 1 | R | Inverter_AC_Input_Fail | INTEGER | N/A | N/A |  | Inverter AC Input Fail
1197 | 0 | 0 | 1 | R | Inverter_Alarm | INTEGER | N/A | N/A |  | Inverter Alarm
1198 | 0 | 0 | 1 | R | Digital_Input_1 | INTEGER | N/A | N/A |  | Digital Input 1
1199 | 0 | 0 | 1 | R | Digital_Input_2 | INTEGER | N/A | N/A |  | Digital Input 2
1200 | 0 | 0 | 1 | R | Digital_Input_3 | INTEGER | N/A | N/A |  | Digital Input 3
1201 | 0 | 0 | 1 | R | Digital_Input_4 | INTEGER | N/A | N/A |  | Digital Input 4
1202 | 0 | 0 | 1 | R | Digital_Input_5 | INTEGER | N/A | N/A |  | Digital Input 5
1203 | 0 | 0 | 1 | R | Digital_Input_6 | INTEGER | N/A | N/A |  | Digital Input 6
1204 | 0 | 0 | 1 | R | Digital_Input_7 | INTEGER | N/A | N/A |  | Digital Input 7
1205 | 0 | 0 | 1 | R | Digital_Input_8 | INTEGER | N/A | N/A |  | Digital Input 8
1206 | 0 | 0 | 1 | R | Load_Voltage | INTEGER | N/A | N/A |  | Load Voltage
1207 | 0 | 0 | 1 | R | PV_Current | INTEGER | N/A | N/A |  | PV Current
1208 | 0 | 0 | 1 | R | Battery_Voltage | INTEGER | N/A | N/A |  | Battery Voltage
1209 | 0 | 0 | 1 | R | Battery_Current | INTEGER | N/A | N/A |  | Battery Current
1210 | 0 | 0 | 1 | R | AC_Mains | INTEGER | N/A | N/A |  | AC Mains
1211 | 0 | 0 | 1 | R | Battery_Temperature | INTEGER | N/A | N/A |  | Battery Temperature
1212 | 0 | 0 | 1 | R | Battery_Runtime | INTEGER | N/A | N/A |  | Battery Runtime
1213 | 0 | 0 | 1 | R | Battery_Capacity | INTEGER | N/A | N/A |  | Battery Capacity
1214 | 0 | 0 | 1 | R | Battery_DOD | INTEGER | N/A | N/A |  | Battery DOD
1215 | 0 | 0 | 1 | R | Converter_Load_Current | INTEGER | N/A | N/A |  | Converter Load Current
1216 | 0 | 0 | 1 | R | Converter_Load_Voltage | INTEGER | N/A | N/A |  | Converter Load Voltage
1217 | 0 | 0 | 1 | R | System_Voltage_Mode | INTEGER | N/A | N/A |  | System Voltage Mode
1218 | 0 | 0 | 1 | R | System_Time_(HH.MM.SS) | INTEGER | N/A | N/A |  | System Time (HH.MM.SS)
1219 | 0 | 0 | 1 | R | System_Date_(YYYY.MM.DD) | INTEGER | N/A | N/A |  | System Date (YYYY.MM.DD)
1220 | 0 | 0 | 1 | R | Total_Rectifier_Current | INTEGER | N/A | N/A |  | Total Rectifier Current
1221 | 0 | 0 | 1 | R | Avg_DC_Voltage | INTEGER | N/A | N/A |  | Avg DC Voltage
1222 | 0 | 0 | 1 | R | Avg_AC_Voltage | INTEGER | N/A | N/A |  | Avg AC Voltage
1223 | 0 | 0 | 1 | R | #_Acquired_Rectifiers | INTEGER | N/A | N/A |  | Acquired Rectifiers
1224 | 0 | 0 | 1 | R | #_Sourcing_Rectifiers | INTEGER | N/A | N/A |  | Sourcing Rectifiers
1225 | 0 | 0 | 1 | R | #_Failed_Rectifiers | INTEGER | N/A | N/A |  | Failed Rectifiers
1226 | 0 | 0 | 1 | R | #_Minor_Alarm_Rectifiers | INTEGER | N/A | N/A |  | Minor Alarm Rectifiers
1227 | 0 | 0 | 1 | R | #_Comms_Lost_Rectifiers | INTEGER | N/A | N/A |  | Comms Lost Rectifiers
1228 | 0 | 0 | 1 | R | #_AC_Failed_Rectifiers | INTEGER | N/A | N/A |  | AC Failed Rectifiers
1229 | 0 | 0 | 1 | R | #_Out_Of_Tolerance | INTEGER | N/A | N/A |  | Out Of Tolerance
1230 | 0 | 0 | 1 | R | #_Locked_Out_Rectifiers | INTEGER | N/A | N/A |  | Locked Out Rectifiers
1231 | 0 | 0 | 1 | R | #_Equalize_Rectifiers | INTEGER | N/A | N/A |  | Equalize Rectifiers
1232 | 0 | 0 | 1 | R | #_Current_Limit_Rectifiers | INTEGER | N/A | N/A |  | Current Limit Rectifiers
1233 | 0 | 0 | 1 | R | #_Power_Limit_Rectifiers | INTEGER | N/A | N/A |  | Power Limit Rectifiers
1234 | 0 | 0 | 1 | R | #_Fan_Failed_Rectifiers | INTEGER | N/A | N/A |  | Fan Failed Rectifiers
1235 | 0 | 0 | 1 | R | #_Power_Saving_Rectifiers | INTEGER | N/A | N/A |  | Power Saving Rectifiers
1236 | 0 | 0 | 1 | R | Avg._AC_Phase_R | INTEGER | N/A | N/A |  | Avg. AC Phase R
1237 | 0 | 0 | 1 | R | Avg._AC_Phase_S | INTEGER | N/A | N/A |  | Avg. AC Phase S
1238 | 0 | 0 | 1 | R | Avg._AC_Phase_T | INTEGER | N/A | N/A |  | Avg. AC Phase T
1239 | 0 | 0 | 1 | R | AC_Output_(VA) | INTEGER | N/A | N/A |  | AC Output (VA)
1240 | 0 | 0 | 1 | R | Source_(%AC) | INTEGER | N/A | N/A |  | Source (%AC)
1241 | 0 | 0 | 1 | R | AC_Output_(W) | INTEGER | N/A | N/A |  | AC Output (W)
1242 | 0 | 0 | 1 | R | DC_Inverter_current_(A) | INTEGER | N/A | N/A |  | DC Inverter current (A)
1243 | 0 | 0 | 1 | R | #_of_Inverters | INTEGER | N/A | N/A |  | of Inverters
1244 | 0 | 0 | 1 | R | #_Invertes_Coms_Lost | INTEGER | N/A | N/A |  | Invertes Coms Lost
1245 | 0 | 0 | 1 | R | #Minor_Alarm_-Inverter | INTEGER | N/A | N/A |  | Minor Alarm -Inverter
1246 | 0 | 0 | 1 | R | #Major_Alarm_-_Inverter | INTEGER | N/A | N/A |  | Major Alarm - Inverter
1247 | 0 | 0 | 1 | R | #Failed_Inverters | INTEGER | N/A | N/A |  | Failed Inverters
1248 | 0 | 0 | 1 | R | FXR_DC_Current | INTEGER | N/A | N/A |  | FXR DC Current
1249 | 0 | 0 | 1 | R | Total_Conv._Current | INTEGER | N/A | N/A |  | Total Conv. Current
1250 | 0 | 0 | 1 | R | Avg_Conv._Output_Voltage | INTEGER | N/A | N/A |  | Avg Conv. Output Voltage
1251 | 0 | 0 | 1 | R | Total_Conv._Input_Current | INTEGER | N/A | N/A |  | Total Conv. Input Current
1252 | 0 | 0 | 1 | R | #_Acquired_Conv. | INTEGER | N/A | N/A |  | Acquired Conv.
1253 | 0 | 0 | 1 | R | #_Failed_Conv. | INTEGER | N/A | N/A |  | Failed Conv.
1254 | 0 | 0 | 1 | R | #_Conv._Minor_Alarm | INTEGER | N/A | N/A |  | Conv. Minor Alarm
1255 | 0 | 0 | 1 | R | #_Conv._In_Comms_Lost | INTEGER | N/A | N/A |  | Conv. In Comms Lost
1256 | 0 | 0 | 1 | R | #_Conv._Input_Voltage_Failed | INTEGER | N/A | N/A |  | Conv. Input Voltage Failed
1257 | 0 | 0 | 1 | R | #_Out_Of_Tolerance_Conv. | INTEGER | N/A | N/A |  | Out Of Tolerance Conv.
1258 | 0 | 0 | 1 | R | #_Conv._In_Current_Limit | INTEGER | N/A | N/A |  | Conv. In Current Limit
1259 | 0 | 0 | 1 | R | #_Conv._Fan_Failed | INTEGER | N/A | N/A |  | Conv. Fan Failed
1260 | 0 | 0 | 1 | R | Timer_1 | INTEGER | N/A | N/A |  | Timer 1
1261 | 0 | 0 | 1 | R | Timer_2 | INTEGER | N/A | N/A |  | Timer 2
1262 | 0 | 0 | 1 | R | Timer_3 | INTEGER | N/A | N/A |  | Timer 3
1263 | 0 | 0 | 1 | R | Timer_4 | INTEGER | N/A | N/A |  | Timer 4
1264 | 0 | 0 | 1 | R | Timer_5 | INTEGER | N/A | N/A |  | Timer 5
1265 | 0 | 0 | 1 | R | Timer_6 | INTEGER | N/A | N/A |  | Timer 6
1266 | 0 | 0 | 1 | R | Timer_7 | INTEGER | N/A | N/A |  | Timer 7
1267 | 0 | 0 | 1 | R | Timer_8 | INTEGER | N/A | N/A |  | Timer 8
1268 | 0 | 0 | 1 | R | Timer_9 | INTEGER | N/A | N/A |  | Timer 9
1269 | 0 | 0 | 1 | R | Timer_10 | INTEGER | N/A | N/A |  | Timer 10
1270 | 0 | 0 | 1 | R | Counter_1 | INTEGER | N/A | N/A |  | Counter 1
1271 | 0 | 0 | 1 | R | Counter_2 | INTEGER | N/A | N/A |  | Counter 2
1272 | 0 | 0 | 1 | R | Counter_3 | INTEGER | N/A | N/A |  | Counter 3
1273 | 0 | 0 | 1 | R | Counter_4 | INTEGER | N/A | N/A |  | Counter 4
1274 | 0 | 0 | 1 | R | Counter_5 | INTEGER | N/A | N/A |  | Counter 5
1275 | 0 | 0 | 1 | R | Counter_6 | INTEGER | N/A | N/A |  | Counter 6
1276 | 0 | 0 | 1 | R | Counter_7 | INTEGER | N/A | N/A |  | Counter 7
1277 | 0 | 0 | 1 | R | Counter_8 | INTEGER | N/A | N/A |  | Counter 8
1278 | 0 | 0 | 1 | R | Counter_9 | INTEGER | N/A | N/A |  | Counter 9
1279 | 0 | 0 | 1 | R | Counter_10 | INTEGER | N/A | N/A |  | Counter 10
1300 | 0 | 0 | 1 | R | Dc_Pwr_Sys_Charge_Volts | INTEGER | N/A | N/A |  | Dc Pwr Sys Charge Volts
1301 | 0 | 0 | 1 | R | Dc_Pwr_Sys_Discharge_Volts | INTEGER | N/A | N/A |  | Dc Pwr Sys Discharge Volts
1302 | 0 | 0 | 1 | R | Dc_Pwr_Sys_Charge_Amps | INTEGER | N/A | N/A |  | Dc Pwr Sys Charge Amps
1303 | 0 | 0 | 1 | R | Dc_Pwr_Sys_Discharge_Amps | INTEGER | N/A | N/A |  | Dc Pwr Sys Discharge Amps
1304 | 0 | 0 | 1 | R | Dc_Pwr_Sys_Major_Alarm | INTEGER | N/A | N/A |  | Dc Pwr Sys Major Alarm
1305 | 0 | 0 | 1 | R | Dc_Pwr_Sys_Minor_Alarm | INTEGER | N/A | N/A |  | Dc Pwr Sys Minor Alarm
1306 | 0 | 0 | 1 | R | Dc_Pwr_Sys_Site_Name | ASCII | N/A | N/A |  | Dc Pwr Sys Site Name
1307 | 0 | 0 | 1 | R | Dc_Pwr_Sys_Site_City | ASCII | N/A | N/A |  | Dc Pwr Sys Site City
1308 | 0 | 0 | 1 | R | Dc_Pwr_Sys_Site_Region | ASCII | N/A | N/A |  | Dc Pwr Sys Site Region
1309 | 0 | 0 | 1 | R | Dc_Pwr_Sys_Site_Country | ASCII | N/A | N/A |  | Dc Pwr Sys Site Country
1310 | 0 | 0 | 1 | R | Dc_Pwr_Sys_Contact_Name | ASCII | N/A | N/A |  | Dc Pwr Sys Contact Name
1311 | 0 | 0 | 1 | R | Dc_Pwr_Sys_Phone_Number | ASCII | N/A | N/A |  | Dc Pwr Sys Phone Number
1312 | 0 | 0 | 1 | R | Dc_Pwr_Sys_Site_Number | ASCII | N/A | N/A |  | Dc Pwr Sys Site Number
1313 | 0 | 0 | 1 | R | Dc_Pwr_Sys_System_Type | ASCII | N/A | N/A |  | Dc Pwr Sys System Type
1314 | 0 | 0 | 1 | R | Dc_Pwr_Sys_System_Serial | ASCII | N/A | N/A |  | Dc Pwr Sys System Serial
1315 | 0 | 0 | 1 | R | Dc_Pwr_Sys_System_Number | ASCII | N/A | N/A |  | Dc Pwr Sys System Number
1316 | 0 | 0 | 1 | R | Dc_Pwr_Sys_Software_Version | ASCII | N/A | N/A |  | Dc Pwr Sys Software Version
1317 | 0 | 0 | 1 | R | Dc_Pwr_Sys_Software_Timestamp | ASCII | N/A | N/A |  | Dc Pwr Sys Software Timestamp
1318 | 0 | 0 | 1 | R | Pwr_Inv_Count | INTEGER | N/A | N/A |  | Pwr Inv Count
1319 | 0 | 0 | 1 | R | Tsi_Modules_Count | INTEGER | N/A | N/A |  | Modules Count
1320 | 0 | 0 | 1 | R | Tsi_Modules_Index | INTEGER | N/A | N/A |  | Modules Index
1321 | 0 | 0 | 1 | R | Tsi_Status_ACOut | INTEGER | N/A | N/A |  | Status ACOut
1322 | 0 | 0 | 1 | R | Tsi_Status_ACIn | INTEGER | N/A | N/A |  | Status ACIn
1323 | 0 | 0 | 1 | R | Tsi_Status_DCIn | INTEGER | N/A | N/A |  | Status DCIn
1324 | 0 | 0 | 1 | R | Tsi_Address | INTEGER | N/A | N/A |  | Address
1325 | 0 | 0 | 1 | R | Tsi_Load_Position | INTEGER | N/A | N/A |  | Load Position
1326 | 0 | 0 | 1 | R | Tsi_Load_Ratio_W | INTEGER | N/A | N/A |  | Load Ratio W
1327 | 0 | 0 | 1 | R | Tsi_Load_Ratio_VA | INTEGER | N/A | N/A |  | Load Ratio VA
1328 | 0 | 0 | 1 | R | Tsi_Serial_Number | INTEGER | N/A | N/A |  | Serial Number
1329 | 0 | 0 | 1 | R | Tsi_Vout | INTEGER | N/A | N/A |  | AC Voltage Output
1330 | 0 | 0 | 1 | R | Tsi_Iout | INTEGER | N/A | N/A |  | AC Current Output
1331 | 0 | 0 | 1 | R | Tsi_Pout_W | INTEGER | N/A | N/A |  | AC Power Output KW
1332 | 0 | 0 | 1 | R | Tsi_Pout_VA | INTEGER | N/A | N/A |  | AC Power Output KVA
1333 | 0 | 0 | 1 | R | Tsi_Vin_AC | INTEGER | N/A | N/A |  | AC Voltage Input
1334 | 0 | 0 | 1 | R | Tsi_Iin_AC | INTEGER | N/A | N/A |  | AC Current Input
1335 | 0 | 0 | 1 | R | Tsi_Pin_ACW | INTEGER | N/A | N/A |  | AC Power Input KW
1336 | 0 | 0 | 1 | R | Tsi_Pin_ACVA | INTEGER | N/A | N/A |  | AC Power Input KVA
1337 | 0 | 0 | 1 | R | Tsi_ACIn_Freq | INTEGER | N/A | N/A |  | AC Input Freq
1338 | 0 | 0 | 1 | R | Tsi_Vin_DC | INTEGER | N/A | N/A |  | DC Voltage
1339 | 0 | 0 | 1 | R | Tsi_Iin_DC | INTEGER | N/A | N/A |  | DC Current
1340 | 0 | 0 | 1 | R | Tsi_Pin_DC | INTEGER | N/A | N/A |  | DC Power KW
1341 | 0 | 0 | 1 | R | Tsi_Temperature | INTEGER | N/A | N/A |  | Max Inverter Temp
1342 | 0 | 0 | 1 | R | Tsi_Soft_Version | INTEGER | N/A | N/A |  | Soft Version
1343 | 0 | 0 | 1 | R | Tsi_Bus_Error_Cnt | INTEGER | N/A | N/A |  | Bus Error Cnt
1344 | 0 | 0 | 1 | R | Tsi_Phase_Number | INTEGER | N/A | N/A |  | Phase Number
1345 | 0 | 0 | 1 | R | Tsi_Status_Mod | INTEGER | N/A | N/A |  | Status Mod
1346 | 0 | 0 | 1 | R | Tsi_Status_AC | INTEGER | N/A | N/A |  | Status AC
1347 | 0 | 0 | 1 | R | Tsi_Status_DC | INTEGER | N/A | N/A |  | Status DC
1348 | 0 | 0 | 1 | R | Tsi_Present | INTEGER | N/A | N/A |  | Present
1349 | 0 | 0 | 1 | R | Tsi_Group_AC | INTEGER | N/A | N/A |  | Group AC
1350 | 0 | 0 | 1 | R | Tsi_Group_DC | INTEGER | N/A | N/A |  | Group DC
1351 | 0 | 0 | 1 | R | Tsi_Restrained | INTEGER | N/A | N/A |  | Restrained
1352 | 0 | 0 | 1 | R | Tsi_No_EPC | INTEGER | N/A | N/A |  | Total No EPC
1353 | 0 | 0 | 1 | R | Tsi_Pout_Nominal_W | INTEGER | N/A | N/A |  | Pout Nominal W
1354 | 0 | 0 | 1 | R | Tsi_Pout_Nominal_VA | INTEGER | N/A | N/A |  | Pout Nominal VA
1355 | 0 | 0 | 1 | R | Tsi_Vin_Nominal_AC | INTEGER | N/A | N/A |  | Vin Nominal AC
1356 | 0 | 0 | 1 | R | Tsi_Vin_Nominal_DC | INTEGER | N/A | N/A |  | Vin Nominal DC
1357 | 0 | 0 | 1 | R | Tsi_Vin_Nominal_Freq_AC | INTEGER | N/A | N/A |  | Vin Nominal Freq AC
1358 | 0 | 0 | 1 | R | Phase_Count | INTEGER | N/A | N/A |  | Phase Count
1359 | 0 | 0 | 1 | R | Phase_Group_Index | INTEGER | N/A | N/A |  | Phase Group Index
1360 | 0 | 0 | 1 | R | B_Ratio_Available_W | INTEGER | N/A | N/A |  | B Ratio Available W
1361 | 0 | 0 | 1 | R | B_Ratio_Available_VA | INTEGER | N/A | N/A |  | B Ratio Available VA
1362 | 0 | 0 | 1 | R | B_Ratio_Installed_W | INTEGER | N/A | N/A |  | B Ratio Installed W
1363 | 0 | 0 | 1 | R | B_Ratio_Installed_WA | INTEGER | N/A | N/A |  | B Ratio Installed WA
1364 | 0 | 0 | 1 | R | W_Vout | INTEGER | N/A | N/A |  | W Vout
1365 | 0 | 0 | 1 | R | W_Iout | INTEGER | N/A | N/A |  | W Iout
1366 | 0 | 0 | 1 | R | B_Nb_Ond_Cfg | INTEGER | N/A | N/A |  | B Nb Ond Cfg
1367 | 0 | 0 | 1 | R | B_Redundancy | INTEGER | N/A | N/A |  | B Redundancy
1368 | 0 | 0 | 1 | R | W_ACOut_Freq | INTEGER | N/A | N/A |  | AC Output Freq
1369 | 0 | 0 | 1 | R | L_Pin_DC | INTEGER | N/A | N/A |  | L Pin DC
1370 | 0 | 0 | 1 | R | L_Pin_ACW | INTEGER | N/A | N/A |  | L Pin ACW
1371 | 0 | 0 | 1 | R | L_Pin_ACVA | INTEGER | N/A | N/A |  | L Pin ACVA
1372 | 0 | 0 | 1 | R | L_Current_Power_In_W | INTEGER | N/A | N/A |  | L Current Power In W
1373 | 0 | 0 | 1 | R | L_Current_Power_In_VA | INTEGER | N/A | N/A |  | L Current Power In VA
1374 | 0 | 0 | 1 | R | L_Installed_Power_In_W | INTEGER | N/A | N/A |  | L Installed Power In W
1375 | 0 | 0 | 1 | R | L_Installed_Power_In_VA | INTEGER | N/A | N/A |  | L Installed Power In VA
1376 | 0 | 0 | 1 | R | L_Available_Power_In_W | INTEGER | N/A | N/A |  | L Available Power In W
1377 | 0 | 0 | 1 | R | L_Available_Power_In_VA | INTEGER | N/A | N/A |  | L Available Power In VA
1378 | 0 | 0 | 1 | R | B_Nb_Inv_Seen | INTEGER | N/A | N/A |  | B Nb Inv Seen
1379 | 0 | 0 | 1 | R | B_Nb_Inv_OK | INTEGER | N/A | N/A |  | B Nb Inv OK
1380 | 0 | 0 | 1 | R | B_Nb_Inv_MO | INTEGER | N/A | N/A |  | B Nb Inv MO
1381 | 0 | 0 | 1 | R | B_Nb_Inv_KO | INTEGER | N/A | N/A |  | B Nb Inv KO
1382 | 0 | 0 | 1 | R | B_Nb_Inv_NT | INTEGER | N/A | N/A |  | B Nb Inv NT
1383 | 0 | 0 | 1 | R | Ac_Group_Count | INTEGER | N/A | N/A |  | Ac Group Count
1384 | 0 | 0 | 1 | R | Ac_Group_Index | INTEGER | N/A | N/A |  | Ac Group Index
1385 | 0 | 0 | 1 | R | Ac_Nb_Inv_OK | INTEGER | N/A | N/A |  | Ac Nb Inv OK
1386 | 0 | 0 | 1 | R | Ac_Nb_Inv_MO | INTEGER | N/A | N/A |  | Ac Nb Inv MO
1387 | 0 | 0 | 1 | R | Ac_Nb_Inv_KO | INTEGER | N/A | N/A |  | Ac Nb Inv KO
1388 | 0 | 0 | 1 | R | Ac_Nb_Inv_Seen | INTEGER | N/A | N/A |  | Ac Nb Inv Seen
1389 | 0 | 0 | 1 | R | Ac_Pin_ACW | INTEGER | N/A | N/A |  | Ac Pin ACW
1390 | 0 | 0 | 1 | R | Ac_Pin_ACVA | INTEGER | N/A | N/A |  | Ac Pin ACVA
1391 | 0 | 0 | 1 | R | Ac_Vin_AC | INTEGER | N/A | N/A |  | Ac Vin AC
1392 | 0 | 0 | 1 | R | Ac_Iin_AC | INTEGER | N/A | N/A |  | Ac Iin AC
1393 | 0 | 0 | 1 | R | Ac_ACin_Freq | INTEGER | N/A | N/A |  | Ac ACin Freq
1394 | 0 | 0 | 1 | R | Ac_ACin_OK | INTEGER | N/A | N/A |  | Ac ACin OK
1395 | 0 | 0 | 1 | R | Dc_Group_Count | INTEGER | N/A | N/A |  | Dc Group Count
1396 | 0 | 0 | 1 | R | Dc_Group_Index | INTEGER | N/A | N/A |  | Dc Group Index
1397 | 0 | 0 | 1 | R | Dc_Nb_Inv_OK | INTEGER | N/A | N/A |  | Dc Nb Inv OK
1398 | 0 | 0 | 1 | R | Dc_Nb_Inv_MO | INTEGER | N/A | N/A |  | Dc Nb Inv MO
1399 | 0 | 0 | 1 | R | Dc_Nb_Inv_KO | INTEGER | N/A | N/A |  | Dc Nb Inv KO
1400 | 0 | 0 | 1 | R | Dc_Nb_Inv_Seen | INTEGER | N/A | N/A |  | Dc Nb Inv Seen
1401 | 0 | 0 | 1 | R | Dc_Pin_DC | INTEGER | N/A | N/A |  | Dc Pin DC
1402 | 0 | 0 | 1 | R | Dc_Vin_DC | INTEGER | N/A | N/A |  | Dc Vin DC
1403 | 0 | 0 | 1 | R | Dc_Iin_DC | INTEGER | N/A | N/A |  | Dc Iin DC
1404 | 0 | 0 | 1 | R | Dc_DCIn_OK | INTEGER | N/A | N/A |  | Dc DCIn OK
1405 | 0 | 0 | 1 | R | Misc_Info_Group_Count | INTEGER | N/A | N/A |  | Misc Info Group Count
1406 | 0 | 0 | 1 | R | Misc_Info_Group_Index | INTEGER | N/A | N/A |  | Misc Info Group Index
1407 | 0 | 0 | 1 | R | B_Old_Version_Number | INTEGER | N/A | N/A |  | B Old Version Number
1408 | 0 | 0 | 1 | R | E_Phase_Number | INTEGER | N/A | N/A |  | E Phase Number
1409 | 0 | 0 | 1 | R | B_Nb_Major | INTEGER | N/A | N/A |  | B Nb Major
1410 | 0 | 0 | 1 | R | W_Tempo_Major_Al | INTEGER | N/A | N/A |  | W Tempo Major Al
1411 | 0 | 0 | 1 | R | Wtempo_Minor_Al | INTEGER | N/A | N/A |  | Wtempo Minor Al
1412 | 0 | 0 | 1 | R | L_Serial_Number | INTEGER | N/A | N/A |  | L Serial Number
1413 | 0 | 0 | 1 | R | B_Nb_Minor | INTEGER | N/A | N/A |  | B Nb Minor
1414 | 0 | 0 | 1 | R | B_Nb_Total_Alarm_Number | INTEGER | N/A | N/A |  | B Nb Total Alarm Number
1415 | 0 | 0 | 1 | R | B_ACInput_Present | INTEGER | N/A | N/A |  | B ACInput Present
1416 | 0 | 0 | 1 | R | B_Saturation_Thresh | INTEGER | N/A | N/A |  | B Saturation Thresh
1417 | 0 | 0 | 1 | R | B_Nb_Groups_DC | INTEGER | N/A | N/A |  | B Nb Groups DC
1418 | 0 | 0 | 1 | R | B_Nb_Groups_AC | INTEGER | N/A | N/A |  | B Nb Groups AC
1419 | 0 | 0 | 1 | R | B_Prog_Relay | INTEGER | N/A | N/A |  | B Prog Relay
1420 | 0 | 0 | 1 | R | B_System_Load_Position | INTEGER | N/A | N/A |  | B System Load Position
1421 | 0 | 0 | 1 | R | W_Soft_Sub_Revision | INTEGER | N/A | N/A |  | W Soft Sub Revision
1422 | 0 | 0 | 1 | R | W_Soft_Main_Revision | INTEGER | N/A | N/A |  | W Soft Main Revision
1423 | 0 | 0 | 1 | R | W_Inv_Version_Text_Error | INTEGER | N/A | N/A |  | W Inv Version Text Error
1424 | 0 | 0 | 1 | R | B_Inv_Max_Know_Parameters | INTEGER | N/A | N/A |  | B Inv Max Know Parameters
1425 | 0 | 0 | 1 | R | Alarm_Group_Count | INTEGER | N/A | N/A |  | Alarm Group Count
1426 | 0 | 0 | 1 | R | Alarm_Group_Index | INTEGER | N/A | N/A |  | Alarm Group Index
1427 | 0 | 0 | 1 | R | B_Device_Number | INTEGER | N/A | N/A |  | B Device Number
1428 | 0 | 0 | 1 | R | B_Event_Type | INTEGER | N/A | N/A |  | B Event Type
1429 | 0 | 0 | 1 | R | W_Event_Number | INTEGER | N/A | N/A |  | W Event Number
1430 | 0 | 0 | 1 | R | S_Event_String | ASCII | N/A | N/A |  | S Event String
1431 | 0 | 0 | 1 | R | Tsi_Pin_ACWH | INTEGER | N/A | N/A |  | Total AC Input Energy
1432 | 0 | 0 | 1 | R | Tsi_Pin_DCWH | INTEGER | N/A | N/A |  | Total DC Input Energy
1433 | 0 | 0 | 1 | R | Tsi_Pout_WH | INTEGER | N/A | N/A |  | Total Output Energy

## Bitfields
DID | Name | Virtual Name | Mask | Value | Description
64110 | OutBack_Error | OutBack_Error_Write_High_Limit | 0x0001 | 0x0001 | High limit last write
64110 | OutBack_Error | OutBack_Error_Write_Low_Limit | 0x0002 | 0x0002 | Low limit last write
64110 | OutBack_Error | OutBack_Error_Write_Invalid | 0x0004 | 0x0004 | Last write invalid
64110 | OutBack_Error | OutBack_Error_DHCP_Failed | 0x0008 | 0x0008 | DHCP failed
64110 | OutBack_Error | OutBack_Error_DNS_Resolve_Failed | 0x0010 | 0x0010 | DNS resolve failure
64110 | OutBack_Error | OutBack_Error_SMTP_Authorization_Failed | 0x0020 | 0x0020 | SMTP authorization failed
64110 | OutBack_Error | OutBack_Error_SMTP_Send_Failed | 0x0040 | 0x0040 | SMTP send failed
64110 | OutBack_Error | OutBack_Error_FTP_Error | 0x0080 | 0x0080 | FTP Error
64110 | OutBack_Error | OutBack_Error_SD_Card_Error | 0x0100 | 0x0100 | SD-Card Error
64110 | OutBack_Error | OutBack_Error_SNTP_failure | 0x0200 | 0x0200 | SNTP failure
64110 | OutBack_Error | OutBack_Error_Write_While_Locked | 0x0400 | 0x0400 | Write while locked
64110 | OutBack_Error | OutBack_Error_Firmware_Update_Not_Supported | 0x0800 | 0x0800 | Device firmware updating not supported
64110 | OutBack_Error | OutBack_Error_Firmware_Update_File_Not_Found | 0x1000 | 0x1000 | Device firmware update file not found
64110 | OutBack_Error | OutBack_Error_Firmware_Update_File_Invalid | 0x2000 | 0x2000 | Device firmware update file invalid
64110 | OutBack_Error | OutBack_Error_Firmware_Update_Failure | 0x4000 | 0x4000 | Device firmware update failure
DID | Name | Virtual Name | Mask | Value | Description
64110 | OutBack_Status | OutBack_Status_Firmware_Update_Complete | 0x0001 | 0x0001 | Firmware Update Complete
DID | Name | Virtual Name | Mask | Value | Description
64110 | OutBack_Update_Device_Firmware_Port | OutBack_FW_Update_Port Number | 0x00FF | N/A | Port Number
64110 | OutBack_Update_Device_Firmware_Port | OutBack_FW_Update_Update_Percentage | 0xFF00 | N/A | Firmware Update Percentage
DID | Name | Virtual Name | Mask | Value | Description
64115 | GS_Split_Error_Flags | GS_Split_Error_Low_VAC | 0x01 | 0x01 | Low AC output voltage
64115 | GS_Split_Error_Flags | GS_Split_Error_Stacking_Error | 0x02 | 0x02 | Stacking error
64115 | GS_Split_Error_Flags | GS_Split_Error_Over_Temp | 0x04 | 0x04 | Over temperature error
64115 | GS_Split_Error_Flags | GS_Split_Error_Low_VDC | 0x08 | 0x08 | Low battery voltage
64115 | GS_Split_Error_Flags | GS_Split_Error_Phase_Loss | 0x10 | 0x10 | Phase loss
64115 | GS_Split_Error_Flags | GS_Split_Error_High_VDC | 0x20 | 0x20 | High battery voltage
64115 | GS_Split_Error_Flags | GS_Split_Error_AC_Shorted | 0x40 | 0x40 | AC output shorted
64115 | GS_Split_Error_Flags | GS_Split_Error_AC_Backfeed | 0x80 | 0x80 | AC backfeed
DID | Name | Virtual Name | Mask | Value | Description
64115 | GS_Split_Warning_Flags | GS_Split_Warning_AC_Input_Frequency_Too_High | 0x01 | 0x01 | AC input frequency too high
64115 | GS_Split_Warning_Flags | GS_Split_Warning_AC_Input_Frequency_Too_Low | 0x02 | 0x02 | AC input frequency too low
64115 | GS_Split_Warning_Flags | GS_Split_Warning_AC_Input_Voltage_Too_Low | 0x04 | 0x04 | AC input voltage too low
64115 | GS_Split_Warning_Flags | GS_Split_Warning_AC_Input_Voltage_Too_High | 0x08 | 0x08 | AC input voltage too high
64115 | GS_Split_Warning_Flags | GS_Split_Warning_AC_Input_Current_Exceeds_Max | 0x10 | 0x10 | AC input current exceeds max
64115 | GS_Split_Warning_Flags | GS_Split_Warning_Temperature_Sensor_Bad | 0x20 | 0x20 | Temperature sensor bad
64115 | GS_Split_Warning_Flags | GS_Split_Warning_Communications_Error | 0x40 | 0x40 | Communications error
64115 | GS_Split_Warning_Flags | GS_Split_Warning_Cooling_Fan_Fault | 0x80 | 0x80 | Cooling fan fault
DID | Name | Virtual Name | Mask | Value | Description
64115 | GS_Split_Sell_Status | GS_Split_Sell_AC_Input_Frequency_Too_High | 0x01 | 0x01 | AC input frequency too high
64115 | GS_Split_Sell_Status | GS_Split_Sell_AC_Input_Frequency_Too_Low | 0x02 | 0x02 | AC input frequency too low
64115 | GS_Split_Sell_Status | GS_Split_Sell_AC_Input_Voltage_Too_Low | 0x04 | 0x04 | AC input voltage too low
64115 | GS_Split_Sell_Status | GS_Split_Sell_AC_Input_Voltage_Too_High | 0x08 | 0x08 | AC input voltage too high
64115 | GS_Split_Sell_Status | GS_Split_Sell_Awaiting_Sell_Delay | 0x10 | 0x10 | Awaiting sell delay
64115 | GS_Split_Sell_Status | GS_Split_Sell_Disabled | 0x20 | 0x20 | Sell disabled
64115 | GS_Split_Sell_Status | GS_Split_Sell_Battery_Voltage_Less_Than_Target | 0x40 | 0x40 | Battery voltage less than target
DID | Name | Virtual Name | Mask | Value | Description
64117 | GS_Single_Error_Flags | GS_Single_Error_Low_VAC | 0x01 | 0x01 | Low AC output voltage
64117 | GS_Single_Error_Flags | GS_Single_Error_Stacking_Error | 0x02 | 0x02 | Stacking error
64117 | GS_Single_Error_Flags | GS_Single_Error_Over_Temp | 0x04 | 0x04 | Over temperature error
64117 | GS_Single_Error_Flags | GS_Single_Error_Low_VDC | 0x08 | 0x08 | Low battery voltage
64117 | GS_Single_Error_Flags | GS_Single_Error_Phase_Loss | 0x10 | 0x10 | Phase loss
64117 | GS_Single_Error_Flags | GS_Single_Error_High_VDC | 0x20 | 0x20 | High battery voltage
64117 | GS_Single_Error_Flags | GS_Single_Error_AC_Shorted | 0x40 | 0x40 | AC output shorted
64117 | GS_Single_Error_Flags | GS_Single_Error_AC_Backfeed | 0x80 | 0x80 | AC backfeed
DID | Name | Virtual Name | Mask | Value | Description
64117 | GS_Single_Warning_Flags | GS_Single_Warning_AC_Input_Frequency_Too_High | 0x01 | 0x01 | AC input frequency too high
64117 | GS_Single_Warning_Flags | GS_Single_Warning_AC_Input_Frequency_Too_Low | 0x02 | 0x02 | AC input frequency too low
64117 | GS_Single_Warning_Flags | GS_Single_Warning_AC_Input_Voltage_Too_Low | 0x04 | 0x04 | AC input voltage too low
64117 | GS_Single_Warning_Flags | GS_Single_Warning_AC_Input_Voltage_Too_High | 0x08 | 0x08 | AC input voltage too high
64117 | GS_Single_Warning_Flags | GS_Single_Warning_AC_Input_Current_Exceeds_Max | 0x10 | 0x10 | AC input current exceeds max
64117 | GS_Single_Warning_Flags | GS_Single_Warning_Temperature_Sensor_Bad | 0x20 | 0x20 | Temperature sensor bad
64117 | GS_Single_Warning_Flags | GS_Single_Warning_Communications_Error | 0x40 | 0x40 | Communications error
64117 | GS_Single_Warning_Flags | GS_Single_Warning_Cooling_Fan_Fault | 0x80 | 0x80 | Cooling fan fault
DID | Name | Virtual Name | Mask | Value | Description
64117 | GS_Single_Sell_Status | GS_Single_Sell_AC_Input_Frequency_Too_High | 0x01 | 0x01 | AC input frequency too high
64117 | GS_Single_Sell_Status | GS_Single_Sell_AC_Input_Frequency_Too_Low | 0x02 | 0x02 | AC input frequency too low
64117 | GS_Single_Sell_Status | GS_Single_Sell_AC_Input_Voltage_Too_Low | 0x04 | 0x04 | AC input voltage too low
64117 | GS_Single_Sell_Status | GS_Single_Sell_AC_Input_Voltage_Too_High | 0x08 | 0x08 | AC input voltage too high
64117 | GS_Single_Sell_Status | GS_Single_Sell_Awaiting_Sell_Delay | 0x10 | 0x10 | Awaiting sell delay
64117 | GS_Single_Sell_Status | GS_Single_Sell_Disabled | 0x20 | 0x20 | Sell disabled
64117 | GS_Single_Sell_Status | GS_Single_Sell_Battery_Voltage_Less_Than_Target | 0x40 | 0x40 | Battery voltage less than target
DID | Name | Virtual Name | Mask | Value | Description
64113 | FX_Error_Flags | FX_Error_Low_VAC | 0x01 | 0x01 | Low AC output voltage
64113 | FX_Error_Flags | FX_Error_Stacking_Error | 0x02 | 0x02 | Stacking error
64113 | FX_Error_Flags | FX_Error_Over_Temp | 0x04 | 0x04 | Over temperature error
64113 | FX_Error_Flags | FX_Error_Low_VDC | 0x08 | 0x08 | Low battery voltage
64113 | FX_Error_Flags | FX_Error_Phase_Loss | 0x10 | 0x10 | Phase loss
64113 | FX_Error_Flags | FX_Error_High_VDC | 0x20 | 0x20 | High battery voltage
64113 | FX_Error_Flags | FX_Error_AC_Shorted | 0x40 | 0x40 | AC output shorted
64113 | FX_Error_Flags | FX_Error_AC_Backfeed | 0x80 | 0x80 | AC backfeed
DID | Name | Virtual Name | Mask | Value | Description
64113 | FX_Warning_Flags | FX_Warning_AC_Input_Frequency_Too_High | 0x01 | 0x01 | AC input frequency too high
64113 | FX_Warning_Flags | FX_Warning_AC_Input_Frequency_Too_Low | 0x02 | 0x02 | AC input frequency too low
64113 | FX_Warning_Flags | FX_Warning_AC_Input_Voltage_Too_Low | 0x04 | 0x04 | AC input voltage too low
64113 | FX_Warning_Flags | FX_Warning_AC_Input_Voltage_Too_High | 0x08 | 0x08 | AC input voltage too high
64113 | FX_Warning_Flags | FX_Warning_AC_Input_Current_Exceeds_Max | 0x10 | 0x10 | AC input current exceeds max
64113 | FX_Warning_Flags | FX_Warning_Temperature_Sensor_Bad | 0x20 | 0x20 | Temperature sensor bad
64113 | FX_Warning_Flags | FX_Warning_Communications_Error | 0x40 | 0x40 | Communications error
64113 | FX_Warning_Flags | FX_Warning_Cooling_Fan_Fault | 0x80 | 0x80 | Cooling fan fault
DID | Name | Virtual Name | Mask | Value | Description
64113 | FX_Sell_Status | FX_Sell_AC_Input_Frequency_Too_High | 0x01 | 0x01 | AC input frequency too high
64113 | FX_Sell_Status | FX_Sell_AC_Input_Frequency_Too_Low | 0x02 | 0x02 | AC input frequency too low
64113 | FX_Sell_Status | FX_Sell_AC_Input_Voltage_Too_Low | 0x04 | 0x04 | AC input voltage too low
64113 | FX_Sell_Status | FX_Sell_AC_Input_Voltage_Too_High | 0x08 | 0x08 | AC input voltage too high
64113 | FX_Sell_Status | FX_Sell_Awaiting_Sell_Delay | 0x10 | 0x10 | Awaiting sell delay
64113 | FX_Sell_Status | FX_Sell_Disabled | 0x20 | 0x20 | Sell disabled
64113 | FX_Sell_Status | FX_Sell_Battery_Voltage_Less_Than_Target | 0x40 | 0x40 | Battery voltage less than target
64113 | FX_Sell_Status | FX_Sell_AC2_Selected | 0x80 | 0x80 | AC2 Selected
DID | Name | Virtual Name | Mask | Value | Description
64118 | FN_Status_Flags | FN_Relay_Status | 0x01 | 0x00 | AUX Relay Disabled
64118 | FN_Status_Flags | FN_Relay_Status | 0x01 | 0x01 | AUX Relay Enabled
64118 | FN_Status_Flags | FN_Charged_Parms | 0x02 | 0x00 | Charged Parms Not Met
64118 | FN_Status_Flags | FN_Charged_Parms | 0x02 | 0x02 | Charged Parms Met
DID | Name | Virtual Name | Mask | Value | Description
64120 | OB_Control_Status | OB_Charging_Absorb | 0x0001 | 0x0001 | Absorb Charging
64120 | OB_Control_Status | OB_Float_Charging | 0x0002 | 0x0002 | Float Charging
64120 | OB_Control_Status | OB_Inverter_AC_Input | 0x0004 | 0x0004 | Inverter AC Input Use
64120 | OB_Control_Status | OB_Inverter_AC_Input | 0x0004 | 0x0000 | Inverter AC Input Drop
64120 | OB_Control_Status | OB_Inverter_Off | 0x0008 | 0x0008 | Inverter Off
64120 | OB_Control_Status | OB_Inverter_Search_Mode | 0x0010 | 0x0010 | Inverter Search Mode
64120 | OB_Control_Status | OB_Inverter_On | 0x0020 | 0x0020 | Inverter On
64120 | OB_Control_Status | OB_Inverter_Grid-Tie | 0x0040 | 0x0040 | Inverter Grid-Tie Enabled
64120 | OB_Control_Status | OB_Inverter_Grid-Tie | 0x0040 | 0x0000 | Inverter Grid-Tie Disabled
64120 | OB_Control_Status | OB_Inverter_Charger_Disabled | 0x0080 | 0x0080 | Inverter Charger Off
64120 | OB_Control_Status | OB_Inverter_Charger_Auto_Mode | 0x0100 | 0x0100 | Inverter Charger Auto Mode
64120 | OB_Control_Status | OB_Inverter_Charger_Bulk_and_Float_Mode | 0x0200 | 0x0200 | Inverter Charger On
64120 | OB_Control_Status | OB_EQ_Charging | 0x0400 | 0x0400 | EQ Charging
64120 | OB_Control_Status | OB_Charging_Bulk | 0x0800 | 0x0800 | Bulk Charging
64120 | OB_Control_Status | OB_SD_Card_Present | 0x1000 | 0x1000 | SD Card Present
64120 | OB_Control_Status | OB_Replay_File_Present | 0x2000 | 0x2000 | Replay File Present
64120 | OB_Control_Status | OB_SD_Card_Error | 0x4000 | 0x4000 | SD Card Error
DID | Name | Virtual Name | Mask | Value | Description
64112 | CCconfig_Faults | CC_Faults_Fault_Input_Active | 0x0010 | 0x0010 | EX80 Fault Input Active
64112 | CCconfig_Faults | CC_Faults_Shorted_Battery_Temp_sensor | 0x0020 | 0x0020 | Shorted Battery Temp sensor
64112 | CCconfig_Faults | CC_Faults_Over_Temp | 0x0040 | 0x0040 | Over Tempurature Fault
64112 | CCconfig_Faults | CC_Faults_VOC_Too_High | 0x0080 | 0x0080 | PV Input voltage too high
DID | Name | Virtual Name | Mask | Value | Description
101 | I_Event_1 | I_Event_1_Battery_Voltage | 0x0002 | 0x0002 | High Battery Voltage
101 | I_Event_1 | I_Event_1_Battery_Voltage | 0x0002 | 0x0000 | Normal Battery Voltage
101 | I_Event_1 | I_Event_1_AC_Input | 0x0004 | 0x0004 | AC Input Disconnected
101 | I_Event_1 | I_Event_1_AC_Input | 0x0004 | 0x0000 | AC Input Connected
101 | I_Event_1 | I_Event_1_Inverter | 0x0040 | 0x0040 | Inverter Off
101 | I_Event_1 | I_Event_1_Inverter | 0x0040 | 0x0000 | Inverter On
101 | I_Event_1 | I_Event_1_Inverter_Temp | 0x0080 | 0x0080 | Inverter Over Temp
101 | I_Event_1 | I_Event_1_Inverter_Temp | 0x0080 | 0x0000 | Inverter Temp Normal
101 | I_Event_1 | I_Event_1_Inverter_AC_Input_Freq_High | 0x0100 | 0x0100 | AC Input Over Frequency
101 | I_Event_1 | I_Event_1_Inverter_AC_Input_Freq_High | 0x0100 | 0x0000 | AC Input Below High Frequency Limit
101 | I_Event_1 | I_Event_1_Inverter_AC_Input_Freq_Low | 0x0200 | 0x0200 | AC Input Under Frequency
101 | I_Event_1 | I_Event_1_Inverter_AC_Input_Freq_Low | 0x0200 | 0x0000 | AC Input Above Lower Frequency Limit
101 | I_Event_1 | I_Event_1_Inverter_AC_Input_Voltage_High | 0x0400 | 0x0400 | AC Input Over Voltage
101 | I_Event_1 | I_Event_1_Inverter_AC_Input_Voltage_High | 0x0400 | 0x0000 | AC Input Below High Voltage Limit
101 | I_Event_1 | I_Event_1_Inverter_AC_Input_Voltage_Low | 0x0800 | 0x0800 | AC Input Under Voltage
101 | I_Event_1 | I_Event_1_Inverter_AC_Input_Voltage_Low | 0x0800 | 0x0000 | AC Input Above Lower Voltage Limit
101 | I_Event_1 | I_Event_1_Inverter_Hardware_Failure | 0x8000 | 0x8000 | Inverter Fan or Temp Sensor Failure
101 | I_Event_1 | I_Event_1_Inverter_Hardware_Failure | 0x8000 | 0x0000 | Inverter Hardware No Faults Detected
DID | Name | Virtual Name | Mask | Value | Description
102 | I_Event_1 | I_Event_1_Battery_Voltage | 0x0002 | 0x0002 | High Battery Voltage
102 | I_Event_1 | I_Event_1_Battery_Voltage | 0x0002 | 0x0000 | Normal Battery Voltage
102 | I_Event_1 | I_Event_1_AC_Input | 0x0004 | 0x0004 | AC Input Disconnected
102 | I_Event_1 | I_Event_1_AC_Input | 0x0004 | 0x0000 | AC Input Connected
102 | I_Event_1 | I_Event_1_Inverter | 0x0040 | 0x0040 | Inverter Off
102 | I_Event_1 | I_Event_1_Inverter | 0x0040 | 0x0000 | Inverter On
102 | I_Event_1 | I_Event_1_Inverter_Temp | 0x0080 | 0x0080 | Inverter Over Temp
102 | I_Event_1 | I_Event_1_Inverter_Temp | 0x0080 | 0x0000 | Inverter Temp Normal
102 | I_Event_1 | I_Event_1_Inverter_AC_Input_Freq_High | 0x0100 | 0x0100 | AC Input Over Frequency
102 | I_Event_1 | I_Event_1_Inverter_AC_Input_Freq_High | 0x0100 | 0x0000 | AC Input Below High Frequency Limit
102 | I_Event_1 | I_Event_1_Inverter_AC_Input_Freq_Low | 0x0200 | 0x0200 | AC Input Under Frequency
102 | I_Event_1 | I_Event_1_Inverter_AC_Input_Freq_Low | 0x0200 | 0x0000 | AC Input Above Lower Frequency Limit
102 | I_Event_1 | I_Event_1_Inverter_AC_Input_Voltage_High | 0x0400 | 0x0400 | AC Input Over Voltage
102 | I_Event_1 | I_Event_1_Inverter_AC_Input_Voltage_High | 0x0400 | 0x0000 | AC Input Below High Voltage Limit
102 | I_Event_1 | I_Event_1_Inverter_AC_Input_Voltage_Low | 0x0800 | 0x0800 | AC Input Under Voltage
102 | I_Event_1 | I_Event_1_Inverter_AC_Input_Voltage_Low | 0x0800 | 0x0000 | AC Input Above Lower Voltage Limit
102 | I_Event_1 | I_Event_1_Inverter_Hardware_Failure | 0x8000 | 0x8000 | Inverter Fan or Temp Sensor Failure
102 | I_Event_1 | I_Event_1_Inverter_Hardware_Failure | 0x8000 | 0x0000 | Inverter Hardware No Faults Detected
DID | Name | Virtual Name | Mask | Value | Description
103 | I_Event_1 | I_Event_1_Battery_Voltage | 0x0002 | 0x0002 | High Battery Voltage
103 | I_Event_1 | I_Event_1_Battery_Voltage | 0x0002 | 0x0000 | Normal Battery Voltage
103 | I_Event_1 | I_Event_1_AC_Input | 0x0004 | 0x0004 | AC Input Disconnected
103 | I_Event_1 | I_Event_1_AC_Input | 0x0004 | 0x0000 | AC Input Connected
103 | I_Event_1 | I_Event_1_Inverter | 0x0040 | 0x0040 | Inverter Off
103 | I_Event_1 | I_Event_1_Inverter | 0x0040 | 0x0000 | Inverter On
103 | I_Event_1 | I_Event_1_Inverter_Temp | 0x0080 | 0x0080 | Inverter Over Temp
103 | I_Event_1 | I_Event_1_Inverter_Temp | 0x0080 | 0x0000 | Inverter Temp Normal
103 | I_Event_1 | I_Event_1_Inverter_AC_Input_Freq_High | 0x0100 | 0x0100 | AC Input Over Frequency
103 | I_Event_1 | I_Event_1_Inverter_AC_Input_Freq_High | 0x0100 | 0x0000 | AC Input Below High Frequency Limit
103 | I_Event_1 | I_Event_1_Inverter_AC_Input_Freq_Low | 0x0200 | 0x0200 | AC Input Under Frequency
103 | I_Event_1 | I_Event_1_Inverter_AC_Input_Freq_Low | 0x0200 | 0x0000 | AC Input Above Lower Frequency Limit
103 | I_Event_1 | I_Event_1_Inverter_AC_Input_Voltage_High | 0x0400 | 0x0400 | AC Input Over Voltage
103 | I_Event_1 | I_Event_1_Inverter_AC_Input_Voltage_High | 0x0400 | 0x0000 | AC Input Below High Voltage Limit
103 | I_Event_1 | I_Event_1_Inverter_AC_Input_Voltage_Low | 0x0800 | 0x0800 | AC Input Under Voltage
103 | I_Event_1 | I_Event_1_Inverter_AC_Input_Voltage_Low | 0x0800 | 0x0000 | AC Input Above Lower Voltage Limit
103 | I_Event_1 | I_Event_1_Inverter_Hardware_Failure | 0x8000 | 0x8000 | Inverter Fan or Temp Sensor Failure
103 | I_Event_1 | I_Event_1_Inverter_Hardware_Failure | 0x8000 | 0x0000 | Inverter Hardware No Faults Detected